2026 Repairs - Teton National Park 2025 Deficiency List

SRLC
Perform 5yr Internal Inspection
Moran Entrance Station
Perform 5yr Internal Inspection Replace 20yr Quick Response Sprinklers
Colter Bay Ranger Station
Perform 5yr Internal Inspection Colter Bay B & U
Perform 5yr Internal Inspection Colter Bay Roads
Perform 5yr Internal Inspection Quarters 1443
Perform 5yr Internal Inspection Test or replace QR Sprinklers 2026
Quarters 1442
Perform 5yr Internal Inspection Test or replace QR Sprinklers 2026
Quarters 1441
Perform 5yr Internal Inspection Test or replace QR Sprinklers 2026
Quarters 1434
Perform 5yr Internal Inspection Replace damaged flow switch. (inop)
Quarters 1427
Perform 5yr Internal Inspection
Replace outdated sprinklers in basement.
Laurence Rockefeller Preserve
Add drain to fire pump test header in pump room for draining test header after pump test. Perform 5yr Internal Inspection
Replace power “ON” bulb on controller Pipe packing drain to floor drain
White Grass Main Cabon
Gauges outdated
4 Lazy F
Perform 5yr Internal Inspection
Provide signage indicating Anti-Freeze has been removed and system is water…
Moulton Main House
Gauges outdated Quarters 1447
Perform 5yr Internal Inspection Quarters 1446
Perform 5yr Internal Inspection Quarters 1454
Gauges outdated

Bird nest on sprinkler at porch Quarters 1455
Perform 5yr Internal Inspection Quarters 1440
Perform 5yr Internal Inspection Quarters 1439
Perform 5yr Internal Inspection Test or replace QR Sprinklers
Craig Thomas VC
Perform 5yr Internal Inspection Quarters 188
Perform 5yr Internal Inspection
Flow switch corroded and does not operate.
Quarters 187 – D
Perform 5yr Internal Inspection Quarters 199
Perform 5yr Internal Inspection Quarters 200
Perform 5yr Internal Inspection Quarters 164 – B
Gauge outdated Quarters 198
Perform 5yr Internal Inspection Quarters 197
Perform 5yr Internal Inspection Quarters 196
Perform 5yr Internal Inspection Quarters 195
Perform 5yr Internal Inspection Quarters 194
Perform 5yr Internal Inspection Quarters 1093
Gauge outdated Quarters 1104
Gauge outdated Quarters 1424
Perform 5yr Internal Inspection
Replace outdated sprinklers in basement Quarters 1423
Perform 5yr Internal Inspection
Replace outdated sprinklers in basement Quarters 1425
Perform 5yr Internal Inspection
Replace outdated sprinklers in basement Quarters 1426
Perform 5yr Internal Inspection
Replace outdated sprinklers in basement
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Quarters 1433
Replace outdated sprinklers Moose Headquarters
Perform 5yr Internal inspection Moose Woodshop
Perform 5yr Internal Inspection Flow did not operate.
Tornado Alley / IT Shop
Alarms did not operate. Repair alarm panel. Perform 5yr Internal Inspection
Granite Entrance Station
Flow switch did not operate. Flow switch appears to be damaged. Perform 5yr Internal Inspection
GTA / Gym
Perform 5yr Internal Inspection
