# 2026 Repairs - Teton National Park 2025 Deficiency List

SRLC

Perform 5yr Internal Inspection

Moran Entrance Station

Perform 5yr Internal Inspection Replace 20yr Quick Response Sprinklers

Colter Bay Ranger Station

Perform 5yr Internal Inspection Colter Bay B & U

Perform 5yr Internal Inspection Colter Bay Roads

Perform 5yr Internal Inspection Quarters 1443

Perform 5yr Internal Inspection Test or replace QR Sprinklers 2026

Quarters 1442

Perform 5yr Internal Inspection Test or replace QR Sprinklers 2026

Quarters 1441

Perform 5yr Internal Inspection Test or replace QR Sprinklers 2026

Quarters 1434

Perform 5yr Internal Inspection Replace damaged flow switch. (inop)

Quarters 1427

Perform 5yr Internal Inspection

Replace outdated sprinklers in basement.

Laurence Rockefeller Preserve

Add drain to fire pump test header in pump room for draining test header after pump test. Perform 5yr Internal Inspection

Replace power “ON” bulb on controller Pipe packing drain to floor drain

White Grass Main Cabon

Gauges outdated

4 Lazy F

Perform 5yr Internal Inspection

Provide signage indicating Anti-Freeze has been removed and system is water…

Moulton Main House

Gauges outdated Quarters 1447

Perform 5yr Internal Inspection Quarters 1446

Perform 5yr Internal Inspection Quarters 1454

Gauges outdated

Bird nest on sprinkler at porch Quarters 1455

Perform 5yr Internal Inspection Quarters 1440

Perform 5yr Internal Inspection Quarters 1439

Perform 5yr Internal Inspection Test or replace QR Sprinklers

Craig Thomas VC

Perform 5yr Internal Inspection Quarters 188

Perform 5yr Internal Inspection

Flow switch corroded and does not operate.

Quarters 187 – D

Perform 5yr Internal Inspection Quarters 199

Perform 5yr Internal Inspection Quarters 200

Perform 5yr Internal Inspection Quarters 164 – B

Gauge outdated Quarters 198

Perform 5yr Internal Inspection Quarters 197

Perform 5yr Internal Inspection Quarters 196

Perform 5yr Internal Inspection Quarters 195

Perform 5yr Internal Inspection Quarters 194

Perform 5yr Internal Inspection Quarters 1093

Gauge outdated Quarters 1104

Gauge outdated Quarters 1424

Perform 5yr Internal Inspection

Replace outdated sprinklers in basement Quarters 1423

Perform 5yr Internal Inspection

Replace outdated sprinklers in basement Quarters 1425

Perform 5yr Internal Inspection

Replace outdated sprinklers in basement Quarters 1426

Perform 5yr Internal Inspection

Replace outdated sprinklers in basement

Quarters 1433

Replace outdated sprinklers Moose Headquarters

Perform 5yr Internal inspection Moose Woodshop

Perform 5yr Internal Inspection Flow did not operate.

Tornado Alley / IT Shop

Alarms did not operate. Repair alarm panel. Perform 5yr Internal Inspection

Granite Entrance Station

Flow switch did not operate. Flow switch appears to be damaged. Perform 5yr Internal Inspection

GTA / Gym

Perform 5yr Internal Inspection