## Sheet1
Attachment 2- Amendment one -Questions and Answers RFQ 6923g226Q000028
Questions | ANSWERS
1. Do you have any recent tank-test information (compliance records (from NYSDEC or Nassau County Health), confirming that the tanks and piping are indeed “tight” and have not leaked? |  | No there is no information regarding this question.
1.1 Please provide, if available: tank registrations; Nassau County or NYSDEC records; prior inspection or testing reports; tank installation or modification records; piping diagrams; monitoring-system information; fuel-system schematics; generator/day-tank information; and any prior environmental reports. If none of these records are available, please confirm that bidders are to base their proposals solely upon conditions observable during the site visit and the written solicitation. |  | None of these records are avalable. Quoters are to base their proposals solely upon conditions observable during the site visit and the written solicitation.
1.2 Please clarify the basis for the decision to permanently remove these tanks at this time. It is our understanding that the tanks may have been inactive for an extended period. Please confirm whether removal was recommended or directed by EPA, NYSDEC, Nassau County Department of Health, USMMA Environmental Compliance, or any other regulatory or environmental authority. |  | No, USMMA decided to remove the tanks due to the use of gas as a fuel sorce.
2. Do you have knowledge of any past fuel releases or spills for these tanks, that would result in the expectation of discovering contaminated soils? |  | No known leaks or spills
2.1 Are there any excavation or site work permits required from the village, town or county? | See Regulatory Engineering Framework in the SOW | See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW- Section Rgulatory Engineering Frame work -Permits and Fees: Yes, the Contractor is solely responsible for procuring, scheduling, and paying for all federal, state, county, and local permits, licenses, and inspections required for both the removal of old tanks and registration/permitting of the new AST or UST systems.
2.2 Please clarify how the Government intends to address materially different site conditions or contamination that cannot reasonably be quantified from the solicitation or site visit. | See Execution Requirments in the SOW. | See Execution Requirments in the See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW
3. Based on current information, it is reasonable to expect the existing fuel oil in these 3 tanks is very old and no longer usable, even with filtering & polishing. Please clarify if our pricing should include filtering, polishing, and transfer to another tank on site…or we should figure on all existing fuel oil to be removed and properly disposed (recommended)? | See Execution Requirments in the SOW. | It is the sole responsibility of the Contractor. See Execution requirements in the See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW
4. Your RFP mentions “…if the fuel cannot be re-used on site...the contractor shall resell the product to the highest bidder…and monetary value credited back to the government…” If deemed not re-usable by USMMA, then the fuel is “bad” and has no value to anyone else. Further, re-selling the fuel has legal taxation implications. We will not re-sell this fuel. Please clarify this requirement. | See Execution Requirments in the SOW. | See Execution requirement in Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW
4.1 We recommend that fuel handling, polishing, transfer, or disposal be established as a unit-price item on a per-gallon basis, and that contaminated soil excavation, transportation, and disposal be established as a unit-price item on a per-cubic-yard basis, based on actual quantities encountered. | See Execution Requirments in the SOW. (Attachment 1-Amendment One) | See Execution requirement in Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW
5. Please provide the exact quantity of fuel oil in each of the (3) tanks. |  | O'Hara 5,963 gross valume remaning Delano Tank #1: 11,207 gross valume remaning Tank#2: 16,673 gross valume remaning. See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW
6. Do you have the depth to groundwater near each of the USTs? |  | Depth of ground water is not known
7. To what extent shall we include removals inside the boiler rooms? (ie: cut & cap the piping just inside the boiler room, remove piping to the pump-sets, remove piping to the pump-sets and also remove the pump-sets, remove ALL fuel oil piping & equipment inside the boiler room, or something else) | See Proect Objective in the Revised SOW (Attachment 1-Amendment One) | The Contractor shall permanently remove from service, extract, and scrap three (3) steel underground storage tanks (USTs) containing No. 2 fuel oil, including all associated piping, wiring, components, and monitoring systems.
8. The boiler rooms for each building have emergency generators that are connected to day-tanks, that are connected to the USTs. Once the (3) USTs are removed, how will the generators be supplied with fuel? | See Revised SOW Phase 4 (Attachment 1-Amendment One) | See the Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW-New Generator Feed Tank Installation
9. What is our responsibility (if any) to reconfigure the piping systems to these generators? | See SOW Phase 4 (Attachment 1-Amendment One) | New Generator Feed Tank Installation
9.1 Please identify whether temporary fuel arrangements, modifications to the existing generator fuel systems, or any other interim measures are required as part of this contract. | See Execution Requirments in the SOW ( Attachment 1-Amendment One) | Temporary Fuel Delivery System: The Contractor shall furnish, install, and maintain a temporary fuel delivery system to ensure the emergency generators at both Delano Hall and O’Hara Hall remain fully operational and available for emergency service throughout the entire duration of the project. The Contractor may utilize the existing facility day tanks at both generator locations to facilitate this temporary fuel feed configuration.
· 9.2 If replacement storage is required, we recommend that installation of appropriately sized replacement tanks, piping, controls, leak detection, and associated work be identified as a separate bid item or separate solicitation so that the required emergency fuel capacity is clearly defined and priced. | See Phase 4 Day Tank Modification (Attachment 1-Amendment One) | Contractor is responsible for conecting existing day tanks to generators per the Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW.
10. At each building, there will be significant disturbances to the existing concrete sidewalks, curbing, asphalt roadways, and landscaping features. Assuming the concrete sidewalks, curbing, and asphalt roadways will be replaced in-kind. However, please clarify your expectations for landscape removals & restoration. (trees, bushes, shrubs, grass, mulch, topsoil, irrigation, etc.—type, species, size, quantities, locations, etc.) Or perhaps it’s best to have the USMMA facility replace the landscaping features (recommended). | See Phase 5 in SOW, Backfill and site restoration(Attachment 1-Amendment One) | The Contractor shall return all work sites and surrounding areas to the exact condition in which they were found prior to the start of work. The Contractor shall assume full financial and operational responsibility for repairing or replacing any damage caused to Academy property, utilities, or vegetation during project execution. See Phase 5. See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW
11. What is the thickness of the existing concrete mats above the tanks? |  | The concrete pads are between 5 and 6 inch thick
12. Can you confirm that the USTs, piping, valves, and the boiler rooms do not have any asbestos, lead paint, or other hazardous materials. |  | The USMMA has no historical information on UST, piping , or valves with any environmental hazards. The boiler room may have lead paint or ACM on heating pipes.
13. Your RFP requests a “firm fixed price”, but there are many undefined work scope items (ie: quantity of fuel, dispose or polish/transfer, existence of contaminated soil, restoration requirements, etc.) Please provide a more detailed work scope or allow unit-pricing for unknown, undisclosed items. | See overall SOW | The Q&A should instead state that contractors are responsible for pricing the work and reasonably foreseeable conditions identified in the solicitation, SOW, and site visit, and that materially differing site conditions will be handled under the applicable contract clauses. FAR 52.236-2, Differing Site Conditions, is included to the RFQ.
14. Are your expectations for the contractor to work at both buildings simultaneously, or one at a time? |  | The contractor may determine the workflow and scheduling of both facilities. The only requirement is that all deliverables are fully completed and met within the defined Period of Performance (POP).
14.1 Please confirm whether offerors are expected to include overtime, premium-time, and holiday-pay costs necessary to maintain the 60-day schedule. |  | No overtime will be allowed. The contractor may determine the workflow and scheduling of both facilities. The only requirement is that all deliverables are fully completed and met within the defined Period of Performance (POP). POP for 60 day schedule will begin with the Contracting Officer's Notice to Proceed. See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW
14.2 Would it be acceptable to utilize steel sheet piling for temporary shoring/support of excavation as necessary for excavation and removing tanks? |  | Yes it is acceptable to use steel sheet piling for shoring support when necessary
15. All soil excavated during the tank removals shall be stockpiled near the excavations. Based on site conditions and proximity of the tanks, all soil stockpiles will be located near or within the existing roadway. Also, these tanks are large and will need to be staged when they are removed from the ground. Please provide clarifications to site access and staging areas during this project (if not the roadway)—with regards to our equipment, trucks, soil stockpiles, etc.. |  | The exact dimensional boundaries of the staging areas, specific allowable parking spaces for haul trucks, and the designated location for tank dismantling will be physically finalized and marked during the mandatory project kick-off/walkthrough with the CO, COR, DPW , and DPS after award.
16. The RFP denotes the period of performance as 60 days, with additional language for liquidated damages/payment for delay. Proper permitting of the project through Nassau County Dept. of Health and getting the existing fuel oil sampled & tested may take several weeks---before any construction can start. Further, if polish & transfer of the fuel is requested or if contaminated soils are discovered, the schedule will be extended. Please clarify your expectations of contract NTP and completion. With the current unknown information, 60 days may be insufficient. |  | Period of Performance of 60 days completion may change based on the unforseen reasons. See answer to question 20.
17. The RFP denotes that 100% performance and payment bonds will be required. Is a bid bond required? |  | Yes per the RFQ.See Attachment 1-Amendment One
18. It is anticipated that you and the government will need ample time to properly respond to all contractor submitted questions. When (what date) should we anticipate your responses and answers? Whenever that date is, I’d like to request 10 business days after that date to properly prepare and submit our proposal. |  | See Amendment one for extension of the RFQ closing date extended to September 11, 2026, 2pm ET.
19. The current due date is September 9th—during the Labor Day holiday period. Many firms and vendors are closed and/or on vacation. Securing proper pricing during this time can be difficult. A one-week extension to September 16 is kindly requested. |  | See Amendment one for extension of the RFQ closing date. See responses to question nubmer 18.
20. Please clarify the intended contract award date, Notice to Proceed date, and required final completion date. Section C states that all work is to be completed within 60 calendar days from contract award. Section F states that the period of performance is 60 days from a TBD date and also references a Base Period of April 1, 2027 through March 31, 2028. Section B identifies a period of September 29, 2026 through September 28, 2027. Please reconcile these dates and identify the actual anticipated 60-day performance window upon which bidders should base their schedules and pricing. |  | Actual anticipated 60 day performance window will begin with Contracting officer's Notice to proceed. (Completion date may change based on unforeseen reasons) after award. See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW
21.Specifically, please confirm whether there will be a defined allowance, unit-price mechanism, contract modification process, or other adjustment for contaminated soil, groundwater, petroleum-contaminated materials, or regulated waste encountered in quantities materially exceeding any Government-provided bidding assumption. |  | Contractors are responsible for pricing the work and reasonably foreseeable conditions identified in the solicitation, SOW, and site visit, and that materially differing site conditions will be handled under the applicable contract clauses.
22. Due to the upcoming holiday, could the bid opening be postponed approximately 2 weeks? |  | See responses to RFQ extension in question number 18.
23.Fuel Handling and Contaminated Soil - Unit Pricing- The solicitation is structured as a Firm Fixed Price requirement; however, the actual quantity and condition of the fuel remaining in the tanks and the quantity of contaminated soil, if any, are not identified. |  | O'Hara 5,963 gross valume remaning Delano Tank #1: 11,207 gross valume remaning Tank#2: 16,673 gross valume remaning See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW
24. Fuel Handling and Contaminated Soil - Unit Pricing- Please provide the estimated gallons of fuel currently contained in each UST and any available information regarding the condition or quality of the fuel. |  | O'Hara 5,963 gross valume remaning Delano Tank #1: 11,207 gross valume remaning Tank#2: 16,673 gross valume remaning See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW
25. We recommend that fuel handling, polishing, transfer, or disposal be established as a unit-price item on a per-gallon basis, and that contaminated soil excavation, transportation, and disposal be established as a unit-price item on a per-cubic-yard basis, based on actual quantities encountered. | See Execution Requirments in the SOW. | See Execution Requirments in the Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW
26. Alternatively, please provide bidding quantities or allowances for these items so that all offerors are pricing the same assumed quantities. | See Execution Requirments in the SOW. | See Execution Requirments in the Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW
27. Existing Fuel Quantity, Polishing, Testing, and Final Disposition - It is our understanding that approximately 35,000 gallons of No. 2 fuel oil remain in the three USTs. Please confirm the estimated quantity in each tank and the total quantity to be managed under this contract. |  | O'Hara 5,963 gross valume remaning Delano Tank #1: 11,207 gross valume remaning Tank#2: 16,673 gross valume remaning See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW
28· Existing Fuel Quantity, Polishing, Testing, and Final Disposition - Please confirm that the required sequence is to pump/remove the fuel, test it for quality, and, where necessary, polish or mechanically clean the fuel to determine whether it is suitable for reuse. | See Execution Requirments in the SOW. | The Government will not manage, take title to, or handle the logistics for any fuel deemed unusable. If the fuel cannot be reused on-site by the Academy, managing the next steps—including navigating any regulatory, legal, or disposal requirements—is the sole responsibility of the Contractor under the contract.See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW section Execution Reqirement.
29.Existing Fuel Quantity, Polishing, Testing, and Final Disposition - If the fuel is determined acceptable for reuse, please confirm whether the Government's intended disposition is transfer to the Kings Pointer vessel and/or another designated Academy storage location, or resale to the highest bidder, with the value or proceeds credited to the Government. | See Execution Requirments in the SOW. | The Government will not manage, take title to, or handle the logistics for any fuel deemed unusable. If the fuel cannot be reused on-site by the Academy, managing the next steps—including navigating any regulatory, legal, or disposal requirements—is the sole responsibility of the Contractor under the contract.See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW section Execution Reqirement.
30· If the fuel cannot meet the required quality standards after polishing and is not suitable for reuse or resale, please confirm that it is to be properly recycled or disposed of in accordance with all applicable requirements, including preparation of all required waste manifests. Please also clarify whether these costs are included in the base Firm Fixed Price or should be priced on a per-gallon basis. | See Execution Requirments in the SOW. | The Government will not manage, take title to, or handle the logistics for any fuel deemed unusable. If the fuel cannot be reused on-site by the Academy, managing the next steps—including navigating any regulatory, legal, or disposal requirements—is the sole responsibility of the Contractor under the contract.See Revised SOW (Attachment 1- Amendment One) section Execution Reqirement.
31· Existing Environmental Conditions and Spill Status - Please confirm whether there is any known or active petroleum spill associated with the three USTs, including any existing or prior NYSDEC spill number. |  | No known leaks or spills
32· Existing Environmental Conditions and Spill Status - Please identify any known soil or groundwater contamination, prior environmental investigation, tank tightness testing, sampling results, or remediation activity associated with the tanks or surrounding areas. |  | No known leaks or spills
33. Existing Environmental Conditions and Spill Status -· If such records exist, please provide them to all offerors. |  | No there is no information regarding this question.
34·Basis for Removal / Regulatory Direction - Please clarify the basis for the decision to permanently remove these tanks at this time. |  | USMMA decided to remove the tanks due to the use of gas as a fuel sorce.
35. Basis for Removal / Regulatory Direction: It is our understanding that the tanks may have been inactive for an extended period. Please confirm whether removal was recommended or directed by EPA, NYSDEC, Nassau County Department of Health, USMMA Environmental Compliance, or any other regulatory or environmental authority. |  | No there is no information regarding this question.
36.Basis for Removal / Regulatory Direction: If removal is based upon any report, recommendation, inspection, notice, correspondence, or regulatory directive, please provide the applicable documentation to all offerors. |  | No there is no information regarding this question.
37· Sixty-Day Completion Requirement and Holiday Impacts Please reconsider the requirement to complete all work within 60 calendar days. The scope includes engineering and permitting, fuel testing and disposition, tank cleaning and removal, excavation, soil sampling and laboratory analysis, potential remediation, backfill, paving/concrete restoration, and project closeout. |  | See responses to question number 20.
38. Sixty-Day Completion Requirement and Holiday Impacts: Depending upon the actual award and Notice to Proceed dates, the 60-calendar-day performance period may extend through upcoming holidays. |  | See responses to question number 20
39· Conflicting Period-of-Performance Dates- Please confirm whether offerors are expected to include overtime, premium-time, and holiday-pay costs necessary to maintain the 60-day schedule. |  | See responses to question number 20. No overtime will be allowed.
40· Conflicting Period-of-Performance Dates - We request that the Government consider extending the performance period to provide adequate time for permitting, laboratory turnaround, unforeseen environmental conditions, weather, holidays, and required restoration. |  | See responses to question number 39 and 20.All work shall be completed within 60 calendar days from the date of Notice to Proceed. (Completion date may change based on unforeseen reasons) after award.
41· Please clarify the intended contract award date, Notice to Proceed date, and required final completion date. |  | Anticipated to award this requirement by end of September 2026.All work shall be completed within 60 calendar days from the date of Notice to Proceed. (Completion date may change based on unforeseen reasons)after award.
42· Emergency Generator Fuel Supply - Delano Hall and O’Hara Hall - It is our understanding that the emergency generators serving Delano Hall and O’Hara Hall utilize day tanks that are presently supplied from the main underground tanks included in this removal project. |  | New Tank Installation Inventory and Locations • Delano Hall & O’Hara Hall: No new bulk storage tanks (ASTs or USTs) will be installed under this contract. The existing facility day tanks at both locations shall be utilized as the primary, permanent fuel source for the emergency generators.
43· Emergency Generator Fuel Supply - Delano Hall and O’Hara Hall- Please confirm whether this understanding is correct and identify the existing fuel source and configuration for each emergency generator. | See Phase 4 Day Tank Modification | Contractor is responsible for conecting existing day tanks to generators, see Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW Tank modification.
44· Emergency Generator Fuel Supply - Delano Hall and O’Hara Hall - If the USTs currently supply these emergency-generator day tanks, please clarify how the Government intends to maintain adequate emergency-generator fuel capacity after the USTs and associated piping are removed. | See Phase 4 Day Tank Modification | Contractor is responsible for conecting existing day tanks to generators see revised SOW, Attachment 1- Amendment one section Phase 4 Day Tank modification.
45· Emergency Generator Fuel Supply - Delano Hall and O’Hara Hall Please identify whether temporary fuel arrangements, modifications to the existing generator fuel systems, or any other interim measures are required as part of this contract. | See Phase 4 Day Tank Modification | Contractor is responsible for conecting existing day tanks to generators see Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW -Tank modification.
46· . Replacement Fuel Storage for Emergency Generators - If removal of the existing USTs eliminates the bulk fuel source for either emergency generator, please confirm whether replacement fuel storage is planned. | See Phase 4 Day Tank Modification | See responses to question number 44, 45.
47· . Replacement Fuel Storage for Emergency Generators - If replacement storage is required, we recommend that installation of appropriately sized replacement tanks, piping, controls, leak detection, and associated work be identified as a separate bid item or separate solicitation so that the required emergency fuel capacity is clearly defined and priced. | See Phase 4 Day Tank Modification | See responses to question number 44, 45.
48·. Replacement Fuel Storage for Emergency Generators - Please advise whether such replacement work is included in the present requirement or will be procured separately. | See Phase 4 Day Tank Modification | See responses to question number 44, 45.
49· Existing Drawings, Tank Records, and Fuel-System Information - The solicitation states that building drawings are not available. Because the scope includes removal of associated piping, wiring, components, and monitoring systems, please provide any other available records that may assist offerors in understanding the existing installation. |  | None of these records are avalable. All Quoters are to base their proposals solely upon conditions observable during the site visit and the revised Statement of Work (See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW) and solicitation.
50· Existing Drawings, Tank Records, and Fuel-System Information - Please provide, if available: tank registrations; Nassau County or NYSDEC records; prior inspection or testing reports; tank installation or modification records; piping diagrams; monitoring-system information; fuel-system schematics; generator/day-tank information; and any prior environmental reports. |  | None of these records are avalable. All Quoters are to base their proposals solely upon conditions observable during the site visit and the revised Statement of Work (Attachment 1- Amendment One) and solicitation.
51·Existing Drawings, Tank Records, and Fuel-System Information - If none of these records are available, please confirm that bidders are to base their proposals solely upon conditions observable during the site visit and the written solicitation. |  | None of these records are avalable. All Quoters are to base their proposals solely upon conditions observable during the site visit and the revised Statement of Work See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW
52· Treatment of Unforeseen Contamination - Please clarify how the Government intends to address materially different site conditions or contamination that cannot reasonably be quantified from the solicitation or site visit. | See Execution Requirments in the SOW. | See Execution Requirments in the Revised SOW(See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW).
53. Due to the upcoming holiday, could the bid opening be postponed approximately 2 weeks? |  | See Amendment One. See the closing date in See Attachment 1-Amendment One -Updated RFQ-
54. Are there any excavation or site work permits required from the village, town or county? | See Regulatory Engineering Framework in the Revised SOW (Attachment 1-Amendment One) | See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOWsection -Permits and Fees: The Contractor is solely responsible for procuring, scheduling, and paying for all federal, state, county, and local permits, licenses, and inspections required for both the removal of old tanks and registration/permitting of the new AST or UST systems.
55. Are any road opening permits required in the event we need to bench our excavation into the existing roadways? | See Regulatory Engineering Framework in the Revised SOW (Attachment 1-Amendment One) | See Regulatory Engineering Framework in the see the Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW)-Permits and Fees: The Contractor is solely responsible for procuring, scheduling, and paying for all federal, state, county, and local permits, licenses, and inspections required for both the removal of old tanks and registration/permitting of the new AST or UST systems.
56. Are there any requirements for backfill compaction? If so, are we required to include costs for any associated soil testing? | Phase 3: Soil Sampling and Site Remediation | See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW) Analytical Testing: Perform independent analytical soil testing at the excavation base and on stockpiled backfill soil to NCDH standards, regardless of whether a spill is suspected
57. Will USMMA restore any existing plantings, bushes/shrubs or trees that require removal? | See Phase 5 in the Revised SOW (Attachment 1- Amendment One), Backfill and site restoration. | The Contractor shall return all work sites and surrounding areas to the exact condition in which they were found prior to the start of work. The Contractor shall assume full financial and operational responsibility for repairing or replacing any damage caused to Academy property, utilities, or vegetation during project execution per the see Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW.
58. During the walkthrough, I saw a couple existing site lamps may need to be removed, stored and reset for us to be able to remove the existing tanks. Could you please confirm that is acceptable? | See Phase 5 in Revised SOW (Attachment -1, Amendment One), Backfill and site restoration. | (See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW)The Contractor shall return all work sites and surrounding areas to the exact condition in which they were found prior to the start of work. The Contractor shall assume full financial and operational responsibility for repairing or replacing any damage caused to Academy property, utilities, or vegetation during project execution.
59. Could you please confirm if there are any existing utilities in close proximity to both work areas? | Revised SOW (Attachment -1, Amendment One) See Regulatory Engineering Framework in the SOW | (See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW)Permits and Fees: The Contractor is solely responsible for procuring, scheduling, and paying for all federal, state, county, and local permits, licenses, and inspections required for both the removal of old tanks and registration/permitting of the new AST or UST systems.
60 Would it be acceptable to utilize steel sheet piling for temporary shoring/support of excavation as necessary for excavation and removing tanks? |  | Yes it is acceptable to use stell sheet piling for shoring support when necessary
61. Are you looking to save the usable existing oil within the UST’s and transfer to another location? | See Execution Requirments in the SOW. | See the revised SOW (Attachment -1, Amendment One) section Execution requirements -Fuel Transfer, Polishing, and Disposition
62. If the answer to question #1 is yes; there appears to be 33,773 gallons of product left, maybe 28,000 good oil, where would it be sent? | See Execution Requirments in the SOW. | See responses to question number 61.
63. If you want to save oil, do you want to polish it first? | See Execution Requirments in the SOW. | See responses to question number 61.
64. Have you determined if there is oil contaminated soil at these locations? |  | No known leaks or spills.
65. Do you require certified clean fill? Or can it just be from a virgin source? | Phase 3: Soil Sampling and Site Remediation | Clean Fill is required. See the Revised SOW (See Attachment 1-Amendment One -Updated RFQ-Section C- Revised SOW) section Phase 3: Soil Sampling and Site Remediation.
66. When was the last time tightness testing was performed on the UST’s? |  | No information available.