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1 [bookmark: 1_PROJECT_DESCRIPTION][bookmark: _Toc230075172]PROJECT DESCRIPTION
1.1 [bookmark: 1.1_DEFINITION_OF_INSTALLATION][bookmark: _Toc230075173]DEFINITION OF INSTALLATION
Installation will be defined as the property and facilities located within the jurisdiction of Hill Air Force Base (AFB), Utah.
1.2 [bookmark: 1.2_PRECEDENCE][bookmark: _Toc230075174]PRECEDENCE
Individual installation specific requirements shall take precedence over the requirements in this section. Specific requirements will be included in the project Statement of Work (SOW.)
1.3 [bookmark: 1.3_PROJECT_DESCRIPTION][bookmark: _Toc230075175]PROJECT DESCRIPTION
The Prime Contractor shall furnish all management, supervision, labor, materials, equipment and incidentals required for a broad range of maintenance, repair and minor construction work on various real property facilities at installations covered under this contract, including design and engineering services incidental to construction. The Contracting Officer (CO) may conduct negotiations with the Prime Contractor and issue individual task orders (TOs) for maintenance, repair and minor construction projects identified by the Base Civil Engineer (BCE), or their approved representative, as part of the Simplified Acquisition of Base Engineering Requirements (SABER) program.
Individual TO projects will vary in size, typically ranging between $25,000 and $5,000,000 including but not limited to trades such as demolition, carpentry, plumbing, electrical, mechanical, painting, welding, pipe fitting, sheet metal, roofing, site work, site utilities, excavation, landscaping, concrete, masonry, pavements, fencing, asbestos and lead base paint abatement, Intrusion Detection Systems (IDS) design and installation, Access Control Systems (ACS) design and installation, fire alarm design and installation, fire suppression design and installation, communication networks and systems, Video Tele-Conference (VTC) and Secure Video Tele-Conference (SVTC) system design and installation and systems furniture removal, repair and installation. However, individual TO projects may exceed $5,000,000 due to repairs, maintenance, and equipment to fulfill project requirements. The Period of Performance (PoP) for this effort is a 5-year base order period with four, 1-year options, and an option to extend 6-months. The total PoP is 9.5 years. 
2 [bookmark: 2_WORK_BY_THE_GOVERNMENT][bookmark: _Toc230075176]WORK BY THE GOVERNMENT
The Government is not obligated to issue any particular type of work under this contract and reserves the right to accomplish work using Government workforces or by other contracts, as the Government deems necessary or desirable, and to do so will not breach or otherwise violate this contract.
3 [bookmark: 3_PERFORMANCE_CAPABILITIES][bookmark: _Toc230075177]PERFORMANCE CAPABILITIES
Competition will be limited to 8(a) firms.  The applicable geographic areas that the Hill AFB SABER contract services are Utah, Nevada, and Wyoming. IAW the SBA contiguous state rule, 8(a) firms competing on this project can establish their bona fide place of business in Arizona, California (Sacramento, Fresno, and Orange County), Colorado, Idaho (Boise District), Montana, Nebraska, Nevada, New Mexico, Oregon, South Dakota, Utah, and Wyoming.  
Offerors with established places of business within the geographic areas listed do not need to establish or re-establish (Utah) a new bona fide place of business. Other 8(a) construction firms that can establish a bona fide place of business within the geographical competitive area within 60 days after award, IAW SBA Policy Notice No. 6000-874794, and the assigned NAICS code will be considered. 
The Prime Contractor shall ensure that all employees and subcontractors have current and valid professional certifications and licenses for their specific position prior to starting work and shall be available at the job site at all times and shall be provided upon request by the Government.
Performance-Based Response Requirement: The Contractor shall, throughout the entire period of performance of this Multiple Award Contract (MAC), maintain the operational capability to have qualified personnel and necessary equipment physically present at any designated task order site within 60 minutes of receiving an emergency service call, and within twenty-four (24) hours for standard daily work orders.

4 [bookmark: 4_KEY_PERSONNEL][bookmark: _Toc230075178]KEY PERSONNEL
Key Contractor employees include: Contract Manager, Project Manager/Superintendent, Quality Control Officer, Environmental Officer and Site Safety and Health Officer. Key Contractor employees shall, as a minimum, meet the requirements listed below. All key personnel must be able to read, write, speak, and understand English.
4.1 [bookmark: 4.1_CONTRACT_MANAGER_(CM)][bookmark: _Toc230075179]CONTRACT MANAGER (CM)
The Prime Contractor shall provide a CM who shall be responsible for the performance of this contract. The name of this person, who shall act for the Contractor, shall be designated in writing to the CO as a part of the management plan.
The CM shall have at least five (5) years of experience in the management of government, commercial, or industrial construction and renovation contracts involving all of the following disciplines: architectural, civil, mechanical, and electrical and communication networks.
The CM shall have full authority to act on behalf of the Contractor on all contractor-related matters for the daily operation of this contract.
The CM shall be available by cellular telephone at all times.
During normal duty hours, the CM shall be available to meet on the installation with government personnel within sixty (60) minutes of notification.
Project or warranty related issues, the CM shall respond as stated below:
1) Non-emergency issues, the Contractor/Subcontractor shall respond to the scene within twenty-four (24) hours of notification and begin repair actions.
2) Emergency issues, the Contractor/Subcontractor shall respond to the scene within sixty (60) minutes of notification and begin repair actions. Examples of emergency work are; work required is to sustain/ensure continued mission operations, unscheduled/undetermined water/electrical outages, no A/C or heat within a facility, imminent danger of Life/Health/Safety of personnel, roof leak directly impacting facility mission.
4.2 [bookmark: 4.2_PROJECT_MANAGER/SUPERINTENDENT][bookmark: _Toc230075180]PROJECT MANAGER/SUPERINTENDENT
The Prime Contractor shall provide a Project Manager/Superintendent that is knowledgeable on all projects they are assigned. The name of this person shall be designated in writing to the CO as a part of the management plan.
The Project Manager/Superintendent shall have at least three (3) years of experience in construction management for similar size/scope projects and be familiar with all aspects of general construction management, practices, methods, and materials.
The Project Manager/Superintendent shall have full authority to act for the Contractor on all matters relating to daily operation of this contract that do not have cost impacts.
The Project Manager/Superintendent shall be available by cellular telephone during normal duty hours.
During normal duty hours, the Project Manager/Superintendent shall be available to meet on the installation with government personnel within sixty (60) minutes of notification.
Project or warranty related issues, the Project Manager/Superintendent shall respond as stated below:
1) Non-emergency issues, the Contractor/Subcontractor shall respond to the scene within twenty-four (24) hours of notification and begin repair actions.
2) Emergency issues, the Contractor/Subcontractor shall respond to the scene within sixty (60) minutes of notification and begin repair actions. Examples of emergency work are; work required is to sustain/ensure continued mission operations, unscheduled/undetermined water/electrical outages, no A/C or heat within a facility, imminent danger of Life/Health/Safety of personnel, roof leak directly impacting facility mission.
4.3 [bookmark: 4.3_QUALITY_CONTROL_OFFICER_(QCO)][bookmark: _Toc230075181]QUALITY CONTROL OFFICER (QCO)
The Prime Contractor shall provide a Quality Control Officer that has at least three (3) years of experience in the area of construction quality control. The Quality Control Officer shall manage the Contractor’s quality control plan. This person shall have the authority to direct Contractor personnel to correct construction deficiencies.
4.4 [bookmark: 4.4_ENVIRONMENTAL_OFFICER][bookmark: _Toc230075182]ENVIRONMENTAL OFFICER
The Prime Contractor shall provide an Environmental Officer to ensure environmental compliance on all projects.
The Environmental Officer shall have and maintain the credentials necessary to be considered a “competent person” as defined by the Federal Asbestos Regulations outlined by the Environmental Protection Agency (EPA), Occupational Safety and Health Administration (OSHA), and the Division of Air Quality.
By OSHA definition, a competent person is a person who “through training or experience is knowledgeable of the various Occupational Safety and Health Administration (OSHA) standards that apply to their workplace, is capable of identifying workplace hazards relating to their specific operations, and has the authority invested in him or her by their employer to correct the hazards to protect their workers.”
The Environmental Officer shall meet the following minimum requirements
1) A minimum of three (3) years of experience working for an environment-oriented organization
2) Have postgraduate qualification from a recognized institution in a related discipline. This includes a masters or postgraduate degree in environmental science, preferably approved by the Chartered Institute of Environmental Health (CIEH).
This individual may perform these duties in conjunction with other duties or this function may be fulfilled by a consulting firm.
The Environmental Officer shall have at least three (3) years of experience in environmental management for construction work. The Environmental Officer shall manage all of the environmental concerns for each project.
4.5 [bookmark: 4.5_SITE_SAFETY_AND_HEALTH_OFFICER_(SSHO][bookmark: _Toc230075183]SITE SAFETY AND HEALTH OFFICER (SSHO)
The Prime Contractor shall provide a Site Safety and Health Officer (SSHO) who shall visit all active work sites a minimum of once per week to perform safety and occupational health management, surveillance, inspections, and safety enforcement for the Contractor to ensure all requirements are met. The Prime Contractor shall provide the SSHO’s inspection findings to the SABER PM weekly or upon completion of the inspection report. Additional inspections may be required if the government finds/determines unsafe, hazardous or unhealthy working conditions exist.
The Quality Control (QC) person may be the SSHO on projects if they possess the qualifications required for Quality Control and SSHO as specified herein. The SSHO shall meet the following requirements:
The SSHO shall be available by cellular telephone during normal duty hours. Level 2 Requirements:
1) A minimum of three (3) years of safety work on similar project.
2) Thirty (30) hour OSHA construction safety class or equivalent within last three (3) years.
3) Competent person training. By OSHA definition, a competent person is a person who “through training or experience is knowledgeable of the various Occupational Safety and Health Administration (OSHA) standards that apply to their workplace, is capable of identifying workplace hazards relating to their specific operations, and has the authority invested in him or her by their employer to correct the hazards to protect their workers.”

4.6 [bookmark: 4.6_CONTRACTOR_AND_SUBCONTRACTOR_EMPLOYE][bookmark: _Toc230075184]DRAFTSMAN

The Prime Contractor shall provide Draftsman personnel possessing a minimum of three (3) years experience specifically dedicated to the drafting and design of construction projects. Designated Draftsman shall demonstrate and apply proficiency in advanced AutoCAD functionalities including, but not limited to, the management of external references, the implementation of standardized layering systems, accurate dimensioning practices, and plotting procedures IOT successfully develop and deliver detailed, compliant drawings for each designated Task Order project. 
4.7 [bookmark: _Toc230075185]CONTRACTOR AND SUBCONTRACTOR EMPLOYEE REQUIREMENTS
Trade Certifications:
1) The Prime Contractor shall ensure that their employees and subcontractor employees have current, valid licenses and certifications necessary to perform their functions. Any cost or time associated with obtaining licenses or certifications shall be at the Contractor’s expense. All prime Contractor employees and subcontractor employees shall have current licenses available at the job site at all times and provide licensing upon request by the Government. If Contractor employee or subcontractor employee is unable to provide license upon request, the Project Manager (PM) will be notified with a request for corrective action. The Contractor employee or subcontractor employee will be removed from the job site and installation until such licenses or certifications are obtained and presented to the CO.
2) Lead Craftsmen/Tradesmen in standard trades must be certified or licensed at the journeyman level (or equivalent for non-standard trades).
General Information:
1) The Prime Contractor shall not employ any person who is or was an employee of the US Government, if the employment of that person would create a real or perceived conflict of interest. Any questions on this issue should be addressed to the CO.
2) The Prime Contractor shall perform fifteen (15) percent or more of the actual construction using prime Contractor personnel. Office and field supervision will not be included in the 15%.
5 [bookmark: 5_MANAGEMENT_PLAN][bookmark: _Toc230075186]MANAGEMENT PLAN
The Prime Contractor shall develop a Management Plan which shall be submitted at the time of proposal. The Management Plan shall be implemented within thirty (30) days of contract award and maintained throughout the duration of the contract. The Management Plan shall include a position description for all key personnel as identified in Section 4, above, required minimum qualifications, and specify which positions are being accomplished by subcontractors. Any subcontractors filling key personnel positions shall have the same authority and certifications required for the positions they are filling. A complete organizational chart shall also be submitted and kept current as part of the management plan.
This plan shall then be continually maintained throughout the life of the Contract by all successful bidders and resubmitted whenever changes in key personnel are made. The Management Plan shall include a position description for all personnel, required minimum qualifications, required job experience (with examples) and specifies which positions are being accomplished by subcontractors. A complete organizational chart shall also be submitted and kept current as part of the management plan. This plan shall be submitted at the time of proposal and shall contain all requirements. The plan shall have a cover sheet that includes the solicitation number, subsequent contract number, Contractor name, address and business phone number. The contents of the plan shall be fully tabulated and a table of contents will be used.
The Contractor’s organizational approach shall provide project management, project engineering, Computer Aided Design (CAD) support, project design, site superintendence, safe working environments, quality control, environmental management, subcontract purchasing and administration and general office administration.
6 [bookmark: 6_SUB-CONTRACTOR_UTILIZATION_PLAN][bookmark: _Toc230075187]SUB-CONTRACTOR UTILIZATION PLAN
The Prime Contractor shall ensure adequate subcontractor pools exist to promote competition, to provide best value to the Government and to meet performance and schedule requirements. The Prime Contractor shall provide a Subcontractor Utilization Plan that demonstrates management of subcontractors, establishment and utilization of subcontractor pools, ability to obtain additional subcontractor resources to meet performance and schedule requirements. This plan will assist the Government in determining if prime Contractors have adequate subcontractor resources and ability to obtain additional subcontractor resources to meet performance and schedule requirements. The Subcontractor Utilization Plan will be submitted and reviewed annually at the beginning of each ordering period; updates may be requested at any time during contract period of performance.
7 [bookmark: 7_DESIGN_AND_CONSTRUCTION_REQUIREMENTS][bookmark: _Toc230075188]DESIGN AND CONSTRUCTION REQUIREMENTS
7.1 [bookmark: 7.1_CONTRACT_DOCUMENTS,_REFERENCE,_STAND][bookmark: _Toc230075189]CONTRACT DOCUMENTS, REFERENCE, STANDARDS, AND PUBLICATIONS
The Prime Contractor shall utilize the referenced documents identified in sections 7.2 and
7.3 below, in the accomplishment of tasks prescribed in TOs. Additional documents, standards, or publications that may be specific to a TO project will be identified in the TO SOW. The standards and publications listed in each section of the specifications, form part of these specifications to the extent referenced. The Prime Contractor shall conform to the provisions of the most recent issue of the listed standard(s) or publication(s).
7.2 [bookmark: 7.2_UNIFIED_FACILITIES_CRITERIA_(UFC)][bookmark: _Toc230075190]UNIFIED FACILITIES CRITERIA (UFC)
The UFC shall be used as the standard building code for all construction under this contract. The UFC website is http://www.wbdg.org/. Any and all changes to the UFC will immediately become requirements of this contract. The UFC references the International Building Code (IBC) 2024 as the basic requirement. The UFC modifies those basic requirements in UFC 01-200-01.
At the time of this SOW, the most current version of UFC 1-200-01 is 01 September 2022, Change 4, 17 December 2024.
7.3 [bookmark: 7.3_INSTALLATION_DESIGN_STANDARDS/PLAN][bookmark: _Toc230075191]INSTALLATION DESIGN STANDARDS/PLAN
Base Facility Design Standard, Hill Air Force Base
The Base Facility Design Standard (BFDS) is intended to alert designers, design-build contractors, facility users, and others of the facility design requirements that are peculiar to Hill AFB including remote sites under the base jurisdiction. This standard supplements or emphasizes established design criteria in government and industry publications including standards, codes, regulations, policies, directives, etc. This standard is being continuously revised and updated as regulations and policies change. Caution must be taken to ensure the latest edition is used. Many governmental jurisdictions have adopted statutes, administrative rules, and/or ordinances that set standards regulating professional practices within their jurisdictions. In addition to the standards set forth herein, said professionals shall also conduct their services in accordance with applicable jurisdictional requirements and standards of practice. Where level of effort differs between the standards set forth herein and any such jurisdictional requirements and/or standards of practice occur, the more stringent requirement(s) shall apply. However, if there are conflicting requirements the government standard will govern.
Architectural Compatibility Plan, Hill Air Force Base
The Architectural Compatibility Plan (ACP) defines a clear design vocabulary to be used throughout Hill AFB, providing specific standards for all aspects of exterior design.
The purpose of the ACP is to define design standards for buildings, site development, and streetscapes that serve to integrate the visual character throughout Hill AFB. The ACP will help ensure consistent quality design decisions.
The ACP sets a minimum standard for quality control, and is intended as a baseline, or beginning point, for the build environment on Hill AFB. All structures, regardless of size, typology, or placement must adhere to the standards set forth in the ACP.
The installation’s BFDS and ACP shall be adhered to on all construction projects. Any possible deviations from these standards shall be brought to the attention of the CO before implementation.
8 [bookmark: 8_QUALITY_CONTROL][bookmark: _Toc230075192]QUALITY CONTROL
8.1 [bookmark: 8.1_GENERAL][bookmark: _Toc230075193]GENERAL
The Prime Contractor shall develop a Quality Control Plan which shall be submitted at the time of proposal and resubmitted whenever changes are made or upon request. The Quality Control Plan shall be implemented within thirty (30) days of contract award and maintained throughout the duration of the contract. The Prime Contractor shall establish, maintain, and implement a complete Quality Control Plan to ensure the requirements of the contract are provided as specified as part of the original solicitation. The Quality Control Plan will be reviewed and accepted by the Government prior to commencement of any work.
The Prime Contractor is responsible for an effective quality control process. The quality control process shall consist of plans, procedures, schedules and organization necessary to manage all TOs to produce end products that comply with contract requirements. The process shall cover all construction operations, both on site and off site, and shall be keyed to the proposed construction sequence.
This plan shall be submitted digitally and shall contain all requirements. The binder shall have a cover sheet that includes the solicitation number, subsequent contract number, Contractor name, address and business phone number. The Quality Control Officer’s name, address and business phone number shall also be included. All listed requirements shall be included. The contents of the binder shall be fully tabulated and a table of contents will be used.
Notification of Noncompliance. The CO will notify the Prime Contractor of any detected noncompliance with the requirements of this section. The Contractor shall take immediate corrective action after receipt of such notice. If the Contractor fails or refuses to comply promptly, the CO may issue an order stopping all or part of the work until satisfactory corrective action has been taken. No part of the time lost due to such stop orders shall be made the subject of claim for extension of time or for excess costs or damages by the Contractor.
8.2 [bookmark: 8.2_QUALITY_CONTROL_PLAN_CONTENTS][bookmark: _Toc230075194]QUALITY CONTROL PLAN CONTENTS
The Quality Control Plan shall identify:
1) Personnel, procedures, instructions, tests, forms, and records to be used.
2) The person within the Contractor’s organization identified as the Quality Control Officer.
3) The authority and responsibilities of all the quality control personnel.
4) Procedures for reviewing and approving all drawings, product data samples or other submittals before submission to the CO. Include procedures for obtaining field measurements.
5) Method of documenting quality control operation, inspection, and testing of both prime and subcontract work including samples of proposed forms.
6) Method of documenting and tracking deficiencies including responsibilities and procedures for correcting deficiencies.
The Government shall review and provide acceptance of the Contractor’s Quality Control Plan.
8.3 [bookmark: 8.3_QUALITY_CONTROL_DOCUMENTATION][bookmark: _Toc230075195]QUALITY CONTROL DOCUMENTATION
The Prime Contractor shall maintain current records (daily construction logs) providing documented evidence that required quality control activities and/or tests have been performed. These records shall be provided to the SABER PM weekly or upon request. These records shall include the work of subcontractors and suppliers and shall be on AF IMT Form 1477 or a form acceptable to the CO that includes, as a minimum, the following information:
1) Contractor/subcontractor and their area of responsibility.
2) Work performed each day, giving location, description, and by whom.
3) Visitors (including inspectors) on site each day.
4) Test and control activities performed with results and references to specifications and drawings requirements. List deficiencies noted along with corrective action.
5) Job safety evaluations stating what was checked, results, and instructions or corrective actions.
6) Instructions given/received and conflicts in plans and/or specifications.
These records shall indicate a description of trades working on the project; the number of personnel working; weather conditions encountered; and any delays encountered. These records shall cover both conforming and deficient features and shall include a statement that equipment and materials incorporated in the work and workmanship comply with the contract.
These records shall be available to government personnel upon request.
8.4 [bookmark: 8.4_COORDINATION_MEETINGS][bookmark: _Toc230075196]COORDINATION MEETINGS
Initial Quality Meeting. After the pre-construction conference and prior to commencement of work for any TO under this contract, the Prime Contractor shall meet with the CO, COR, and SABER Representative to discuss the Contractor’s Quality Control Plan. During the meeting, a mutual understanding of the plan details shall be developed, including the forms for recording quality control operations, control activities, testing, administration of the system for both on site and off site work, and the interrelationship of Contractor's management and control with the government's quality assurance. Minutes of the meeting shall be prepared by the Contractor and signed by both the SABER Representative and the CO. The minutes shall become a part of the contract file. There may be occasions when subsequent conferences will be called by either party to reconfirm mutual understandings and/or address deficiencies in the quality control system or procedures that may require corrective action by the Contractor.
Interface with Government Inspectors. The Quality Control Officer may request meetings with the Government, through the CO, to discuss quality issues when they arise. The Government reserves the right to conduct quality meetings at its discretion.
9 [bookmark: 9_BID,_PERFORMANCE_AND_PAYMENT_BONDS][bookmark: _Toc230075197]BID, PERFORMANCE AND PAYMENT BONDS
Bid Bonds will be required In Accordance With (IAW) Federal Acquisition Regulation (FAR) 52.228-1 and 52.228-2 as specified at the TO level. Performance and Payment Bonds will be required IAW FAR Clause 52.228-15 and due not later than ten (10) days after award notification. A minimum blanket bond capacity of $5 million for SABER TOs is required.
Additional bonding will be required if active SABER projects exceed $5 million.
10 [bookmark: 10_PROTECTION_OF_CONTRACTOR’S_EQUIPMENT_][bookmark: _Toc230075198]PROTECTION OF CONTRACTOR’S EQUIPMENT AND GOVERNMENT PROPERTY
10.1 [bookmark: 10.1_FURNITURE_AND_EQUIPMENT][bookmark: _Toc230075199]FURNITURE AND EQUIPMENT
For each TO, the SABER PM and the Prime Contractor shall coordinate with occupants of the proposed work area on responsibilities of moving furniture and equipment. If the Contractor moves the furniture, associated costs may be included in the proposal. The Government shall hold the Contractor responsible for any damages when the Contractor moves the furniture.
The Contractor shall cover all equipment, material, furniture, etc., that is to remain in place within the contract operations area and protect it against damage or loss. The Contractor shall store, protect and clean all equipment, material, furniture, etc. that is removed by the Contractor during the performance of work where directed, or reused in work as required by the TO SOW, drawings, or specifications. All equipment, material, furniture, etc. removed by the Contractor shall be stored, protected and cleaned prior to reuse, or replaced with exact kind if damaged or lost. All equipment, material, furniture, etc. shall be in equal to or better than its original condition upon completion of the TO. Security for all equipment or material that is to be reused and is removed for temporary storage shall be the sole responsibility of the Prime Contractor.
The Prime Contractor shall take an inventory of all items to be stored outside the work area and provide a copy to the SABER PM. The inventory list shall indicate the item name, any visible damage and location of storage. Accompanying photographs are acceptable and preferred. Photographs shall clearly show any existing damage prior to project start or the removal of any equipment, material, furniture, etc. to be stored by the Contractor. Failure to provide evidence of existing damage shall result in the Contractor replacing the equipment, material, furniture, etc. with exact kind.
10.2 [bookmark: 10.2_DAMAGE_TO_GOVERNMENT_REAL_PROPERTY][bookmark: _Toc230075200]DAMAGE TO GOVERNMENT REAL PROPERTY
Any damage done by the Contractor to existing government real property shall be repaired to a prior to damage condition. The Contractor shall patch and repair any damage done to walls, floors, ceilings, doors, etc. during the removal of any items or materials. Contractor repairs shall match the existing conditions, present an undisturbed appearance and meet the requirements of these specifications. CE will determine if repair work is sufficient and acceptable. All repair work will be at the Contractor’s expense.
10.3 [bookmark: 10.3_ELECTRICAL_SERVICE_AND_COMMUNICATIO][bookmark: _Toc230075201]ELECTRICAL SERVICE AND COMMUNICATIONS FACILITIES
The Contractor will not disturb electrical and/or communications facilities and wiring. Where such facilities require equipment removal for the accomplishment of the project work, the Contractor shall notify the CO in writing at least ten (10) calendar days in advance of the requirement, for the accomplishment of such removal work by the Government. The Contractor shall allow the utility owner enough time to remove the systems required. If damaged by Contractor’s construction activities, the Contractor shall restore service within twenty-four (24) hours with no cost to the government.
11 [bookmark: 11_PROVISIONS_ON_CONTRACTING_OFFICER’S_A][bookmark: _Toc230075202]PROVISIONS ON CONTRACTING OFFICER’S AUTHORITY
Only the CO is authorized to make changes to the contract or any TO issued thereunder. No other Government or non-Government official may alter this contract or any TO issued in accordance with the basic contract terms and conditions. The Contractor is to report any attempts to alter this contract or any TO, to the CO. IN THE EVENT THE CONTRACTOR EFFECTS ANY SUCH CHANGE(S) AT THE DIRECTION OF ANY PERSON OTHER THAN THE CO, THE CHANGE(S) WILL BE CONSIDERED TO HAVE BEEN MADE WITHOUT AUTHORITY AND NO ADJUSTMENT WILL BE MADE IN THE CONTRACT PRICE TO COVER ANY INCREASE IN COSTS INCURRED AS A RESULT THEREOF.
12 [bookmark: 12_GOVERNMENT_CONTRACT_ADMINISTRATION][bookmark: _Toc230075203]GOVERNMENT CONTRACT ADMINISTRATION
Contracting Officer (CO): Government official authorized to enter into, make changes to, or terminate contracts on behalf of the United States (US) Government. COs are responsible for ensuring performance of all necessary requirements of the contract, to ensure compliance with the terms of the contract, and safeguard the interests of the US Government in its contractual relationships.
13 [bookmark: 13_CONSTRUCTION_START-UP_PERIOD][bookmark: _Toc230075204]CONSTRUCTION START-UP PERIOD
From the date of contract award, the first thirty (30) calendar days shall be designated as a start-up period during which the Contractor shall have all equipment and personnel in place and mobilization activities associated with this contract fully executed and ready to fulfill the requirements of this contract.
14 [bookmark: 14_PRE-PERFORMANCE_CONFERENCES][bookmark: _Toc230075205]PRE-PERFORMANCE CONFERENCES
Before work begins on this contract, the CO will arrange for a meeting with the Contractor to discuss the contract in general, including administrative matters, project requirements, submittal procedures, approvals and payment schedule, quality control expectations, Fair Opportunity Proposal Request (FOPR) and TO procedures, traffic control, construction access requirements, as-built criteria, performance requirements, security procedures, accident prevention, safety and fire prevention briefings.
15 [bookmark: 15_TASK_ORDERING_PROCEDURES][bookmark: _Toc230075206]TASK ORDERING PROCEDURES
15.1 [bookmark: 15.1_FAIR_OPPORTUNITY_PROPOSAL_REQUEST_(][bookmark: _Toc230075207]FAIR OPPORTUNITY PROPOSAL REQUEST (FOPR)
For each project, the Prime Contractor will be furnished with one electronic copy of the TO SOW. The Contractor may also be provided with one set of drawings and/or specifications, if available. All attachments to the TO FOPR, if applicable, will be considered to be a part of the project scope of work. The level of design provided to the Contractor shall be a written narrative describing the basic concept of the TO. The Contractor may reproduce any drawings and specifications at the Contractor’s own expense, if additional copies are needed. The Contractor shall check all drawings and specifications provided by the government immediately upon receipt for discrepancies and notify the CO immediately of any and all discrepancies found in the form of a Request for Information (RFI). Enlarged plans and details shall govern where the same work is shown at smaller scales. The Contractor shall review all Government provided drawings and verify the information for accuracy prior to proposing on TOs and shall be responsible for any errors which might have been avoided thereby. All Government provided drawings are for reference only unless otherwise stated in the TO SOW.
TO FOPR: A pre-proposal site visit will be held between the Government and the Contractor as requested in the TO FOPR, to discuss all conditions and details of the proposed TO. The Contractor shall submit questions\clarification in writing, IAW FOPR instructions. On average, the Period of Performance (PoP) of a TO is 120 days. However, each TO will identify the specific PoP for that project.
The Contractor shall provide lead times for all material requiring eight (8) weeks or more for delivery in their proposals.
15.2 [bookmark: 15.2_SITE_VISIT][bookmark: _Toc230075208]SITE VISIT
The Government and Contractor(s) will conduct a pre-proposal site visit for each TO. Discussions may include, but are not limited to: scope of work, method of construction, sequence of operations, progress schedule, means of access to project site, delivery and storage of materials and equipment, work restrictions, coordination requirements, project goals, liquidated damages and potential difficulties/problems. The Contractor shall submit Request for Information (RFI) questions within seven (7) days of initial site visit or as directed in the TO specific FOPR.
15.3 [bookmark: 15.3_ON-SITE_CONDITIONS][bookmark: _Toc230075209]ON-SITE CONDITIONS
Drawings, if provided, showing the location of equipment, piping, ducts, conduit, etc. are conceptual and may not show every detail required. In addition, site conditions will not always permit installation in the locations shown. Drawings showing equipment, piping, ducts, conduit, etc. to be removed, altered, or installed may require deviation from the configuration of the demolition or installation drawings due to existence of conflicting ducts, conduits, hangers, light fixtures, structural items, and temporary walls, etc. All such minor details of work which are not shown on the drawings, as well as such items not specifically mentioned in the specifications, but which are essential and necessary for the completion of the work, and to make all systems or equipment operational, shall be considered as incidental and shall be included as part of the work. When this situation occurs, the final placement of permanently installed items shall be subject to approval by the applicable CO.
All drawings provided by the government shall be considered conceptual unless otherwise stated in the TO SOW. The Contractor shall be responsible for inspecting to their satisfaction, all areas and/or items of possible conflict. Failure to verify the dimensions, locations, equipment specifications (both existing and new) and the facilities supporting utilities will be at the Contractor's risk and shall not relieve the Contractor from accomplishing the work required by the TO.
15.4 [bookmark: 15.4_PROJECT_PROPOSAL][bookmark: _Toc230075210]PROJECT PROPOSAL
Individual project proposals shall follow instructions in each TO’s FOPR. The Contractor shall submit the proposal within the time identified in the TO FOPR, typically fourteen (14) calendar days from date of site visit. However, TO FOPR response dates may vary depending upon the complexity of the project, urgency, and end of fiscal year requirements.
15.4.1 [bookmark: 15.4.1_CONSTRUCTION_SCHEDULE][bookmark: _Toc230075211]CONSTRUCTION SCHEDULE
A construction schedule is required IAW FAR 36.515 and FAR 52.236-15 for projects with a continuous performance period of sixty (60) days or more. Additionally, the Contractor shall submit a construction schedule when required by the TO SOW. The construction schedule shall be on an AF Form 3064 and completed according to the instructions on the reverse side of the form. In addition to the construction schedule on the AF Form 3064, the TO SOW may require a project to have a critical path or milestone schedule. The Contractor shall provide weekly construction updates on each TO on an AF Form 3065.
15.4.2 [bookmark: 15.4.2_DESIGN_SOLUTION][bookmark: _Toc230075212]DESIGN SOLUTION
The Contractor shall provide, as part of the proposal, a basic design solution in narrative format or drawings. Drawings included with the proposal must be thorough enough to allow the Government to determine the Contractor has a complete understanding of the project scope. Design incidental to accomplishing the required tasks outlined in each TO will be required. Typically, Contractor maximum design for SABER is up to 35%. If the design requires the services of a registered architect or engineer, it is generally outside the parameters of minimum design; however, in some situations specific building codes may require a licensed engineer or architect for certain elements of a project. As an example, a licensed engineer may be required for certain components of a fire suppression system to be replaced or repaired and a fire suppression engineer may be required to sign off on changes to the system. The extent of these designs will depend upon the complexity of each task. Also, designs shall clearly illustrate compliance with local, state, and federal building construction codes. Contractors are not required to bid on projects that exceed 35% design. As required in the SOW or otherwise required, the Contractor shall include the following documentation at a minimum in the TO proposal:
1) Shop drawings showing basic layout and planning of work.
2) Design Calculations
The Contractor shall provide as part of the proposal, design calculations to substantiate appropriate equipment or material selection/sizing, component assembly and proposed layout and sizing of utilities and structural elements. The Contractor shall, at a minimum, supply the following calculation as required per TO:
a. Mechanical: HVAC load analysis and unit sizing, pipe sizing, and duct sizing.
b. Electrical: Electrical system capacity, conductor, conduit, protective devices and other equipment sizing.
c. Structural: Structural system and foundation sizing.
d. Pavement/Site Work: Area run-off quantities, drainage capacities, and grading slopes.
e. Energy: Provide energy savings and Return on Investment (ROI).
15.4.3 [bookmark: 15.4.3_TASK_ORDER_PRICING][bookmark: _Toc230075213]TASK ORDER PRICING
Pricing: Pricing fairness and reasonableness will be established by adequate price competition. For instances when only one quote is received or found technically acceptable, price fairness and reasonableness will be established by price analysis. Depending on the project or TO, a Division Cost breakout or lump sum proposal may be acceptable. However, for proposals where the Government does not find the prices fair and reasonable, the Government may require Data Other than Certified Cost or Pricing Data as outlined in FAR
15.402. Data Other than Certified Cost or Pricing Data may be required from subcontractors. This data may include established catalog or market prices, sales to non-governmental and governmental entities.
Competition in Subcontracting: The Prime Contractor shall select subcontractors (including suppliers) on a competitive basis to the maximum extent practical consistent with the objectives and requirements of the contract.
15.4.4 [bookmark: 15.4.4_SUBMISSION_OF_TO_FOPR][bookmark: _Toc230075214]SUBMISSION OF TO FOPR
The Contractors shall be requested to submit the TO proposal to the issuing office within the period stated in the TO FOPR which may consist of:
1) Technical Proposal. Concept sketches or drawings for proposed methods, performance schedule of design and construction, proposed technical approach/solution, list of required work elements, management approach, key personnel and/or subcontractors, catalogs, and/or other material submittals.
2) Price Proposal. The price proposal for the design and construction cost.
3) Past Performance. Recent and relevant performance information may be required. Definitions of "recent" and “relevant” will be specified in the TO FOPR for each project.
The Contractor shall follow all instructions within the TO FOPR.
The TO proposals shall be prepared at no cost to the Government, and are not reimbursable by the Government.
16 [bookmark: 16_TASK_ORDER_PROPOSAL_EVALUATION][bookmark: _Toc230075215]TASK ORDER PROPOSAL EVALUATION
Unless the CO applies the exceptions per FAR 16.505(b)(2), each TO will be awarded, as a result of competition, to the Contractor who offers the best value to the Government considering the criteria specified in the TO.
16.1 [bookmark: 16.1_TO_EVALUATION_CRITERIA][bookmark: _Toc230075216]TO EVALUATION CRITERIA
Individual TOs will be competed equally among all awardees after award of the seed project IAW FAR 16.505(b), Fair Opportunity. TOs will be firm fixed price and will clearly define the specific work required. SABER TO awards will be made on a best value basis determined by Lowest Price Technically Acceptable (LPTA), Tradeoff, or Low Price. Specific instructions to Offerors and evaluation criteria for individual TOs will be specified in the TO FOPR. The TO source selection method will be selected at the discretion of the Government in consideration of the project scope, complexity, magnitude, and urgency.
16.2 [bookmark: 16.2_COMPETITION][bookmark: _Toc230075217]COMPETITION
All SABER contractors will be solicited for each project. SABER contractors are encouraged to participate in all site visits and shall submit proposals for all funded TOs. Failure to participate responsibly in site visits and proposal submissions may be reflected in Contractor Performance Assessment Reporting System (CPARS) ratings. Contractors may request a proposal submittal exemption in writing to the CO within five (5) calendar days of issuance of TO FOPR with rationale for not participating. However, when the TO FOPR contains FAR Clause 52.232-18, Availability of Funds, submission of proposals for those projects is at the sole discretion of the respective Contractors and their declination to participate in any or all such solicitations will not be negatively reflected.
16.3 [bookmark: 16.3_PERFORMANCE_EVALUATIONS][bookmark: _Toc230075218]PERFORMANCE EVALUATIONS
At the conclusion of each TO or other times as determined appropriate by the CO or SABER PM, the Contractor’s performance evaluation will be made through the CPARS. The evaluation will take into account all aspects of the Contractor’s performance. The Contractor will be provided an opportunity to review and comment to the government evaluation result through the CPARS. Past performance may be used during TO evaluations, which may have an impact on the award of the TO. Past Performance evaluations are not limited to the CPARS ratings only and may include, but is not limited to, get well ratings or PM input.
17 [bookmark: 17_COMMENCEMENT,_EXECUTION,_COMPLETION_A][bookmark: _Toc230075219]COMMENCEMENT, EXECUTION, COMPLETION AND PAYMENT FOR WORK
17.1 [bookmark: 17.1_ISSUE_OF_NOTICE_TO_PROCEED_(NTP)][bookmark: _Toc230075220]ISSUE OF NOTICE TO PROCEED (NTP)
Upon award of a TO, the Contractor shall have fourteen (14) calendar days to provide the CO with a project start date. This will allow for subcontracting contracts to be awarded, material lead times to be determined and a drawing timeframe to be established and taken into consideration when developing a project start date. The time to develop project Shop Drawing’s should not exceed thirty (30) days on average. The project start date will be evaluated and approved/disapproved based on the Contractors current work load, material lead times and the customer’s readiness to support the project. The CO may negotiate the project start date if the provided date is not satisfactory for all.
The Contractor shall provide a complete set of project Shop Drawings to the CO for approval prior to the NTP start date and before beginning any work at the project site. Failure to provide acceptable shop drawings prior to the agreed upon project start date shall not be cause for a time extension to the contract. Any additional time needed to develop and finalize drawings shall be deducted from the overall project PoP.
17.2 [bookmark: 17.2_MEETINGS][bookmark: _Toc230075221]MEETINGS
The Contractor shall ensure key management personnel participate in and provide briefings to the Base Civil Engineer (BCE), or Director of Public Works (DPW), if requested. The BCE or DPW may be represented by the SABER PM.
The Contractor’s CM and PM, at a minimum, will interact in the form of conferences, meetings and reviews on a bi-weekly basis with government personnel regarding the performance and status of their respective TOs, when the government deems necessary. The CO may decide to reduce the frequency of meetings if needed. The purpose of these meetings is to discuss the status of active projects, schedules, projections, problems, corrective actions, recommendations, etc., to help accomplish program and project goals.
The Contractor shall provide a written listing of all active projects and shall include at a minimum: project name, project number, TO number, TO completion date, scheduled completion date, project status and pertinent remarks. The listing shall be prepared by the Contractor in advance of the scheduled bi-weekly meeting and copies of the listing shall be provided to all personnel in attendance. Contracting representatives and other government personnel may also attend these bi-weekly meetings. The CO shall determine the date and time for the weekly meetings.
18 [bookmark: 18_OPERATIONAL/WORK_INTERUPTIONS_AND_WEA][bookmark: _Toc230075222]OPERATIONAL/WORK INTERUPTIONS AND WEATHER DELAYS
The Contractor may be required to temporarily stop work for operational requirements, special events, installation exercises, or while Distinguished Visitor (DV) familiarization visits/tours are conducted. Official late reporting and snow calls may affect the Contractor’s work periods. The Contractor shall make allowances for these events and resulting lost time will not be reimbursable. Notification to the Contractor shall be provided by the CO.
The Contractor and their personnel shall leave Hill AFB upon notification by the CO or constituted authority when directed that operational requirements or emergencies dictate.
Official snow call or late reporting may affect the Contractor’s production for which the CO will not consider reimbursement for lost work time. Normal delay should not exceed one (1) hour in duration, but may.
Inclement weather, operational delays, and security related delays might affect the Contractor’s work periods. The Contractor must make allowances for these events, as resulting lost time will not be reimbursable.
When working in any of the Munition Storage Areas (MSA), the Contractor may be unable to access the work site due to no-notice inspections. If this happens, the government will allow for a time extension, if needed, on a one day for one day exchange. Inspections of the MSA’s only occur about once a year, but may happen more frequently.
19 [bookmark: 19_HOURS_OF_WORK][bookmark: _Toc230075223]HOURS OF WORK
The Contractor shall complete the work of projects between the hours of 7:00 a.m. and 4:00 p.m. local time, excluding Saturdays, Sundays, and Federal Holidays unless otherwise specified in the TO SOW. Access to work sites may be restricted to these hours and days. The Contractor may not work during non-standard hours unless the request and justification is approved by the CO. The Contractor must submit a request and justification for working non-standard hours to the CO at least 5 working days prior to working non-standard hours. Work that requires inspection during accomplishment or that prevents inspection of other work after accomplishment must be coordinated with and approved in advance by the CO.
The Government recognizes the following legal holidays established by federal statute:
1) New Year's Day, 1 January
2) Martin Luther King Day, third Monday in January
3) President’s Day, third Monday in February
4) Memorial Day, last Monday in May
5) Juneteenth, June 19
6) Independence Day, 4 July
7) Labor Day, first Monday in September
8) Columbus Day, second Monday in October
9) Veteran's Day, 11 November
10) Thanksgiving Day, fourth Thursday in November
11) Christmas Day, 25 December

Family Days designated by the Wing Commander will also be recognized by the Government.
20 [bookmark: 20_JOBSITE_VERIFICATION][bookmark: _Toc230075224]JOBSITE VERIFICATION
It is the Contractor’s responsibility to verify all dimensions, locations, equipment specifications (both existing and new) and the facilities supporting utilities. Failure to do so will be at the Contractor's risk and shall not relieve the Contractor from accomplishing the work required by the TO. This is not a justification for a contract modification.
21 [bookmark: 21_MATERIAL_SUBMITTALS][bookmark: _Toc230075225]MATERIAL SUBMITTALS
21.1 [bookmark: 21.1_GENERAL][bookmark: _Toc230075226]GENERAL
FAR Clauses "FAR 52.236-5, Material and Workmanship," and "FAR 52.236-21, Specifications and Drawings for Construction," apply to all submittals.
The Contractor shall provide submittals as required by the TO SOW. The CO may request submittals in addition to those specified when deemed necessary to adequately describe the work covered in the respective sections. Units of weights and measures used on all submittals shall be the same as those used in the TO SOW and/or Shop Drawings. Each submittal shall be complete and in sufficient detail to allow ready determination of compliance with contract requirements. Prior to submission, all material and equipment submittals and shop drawings shall be checked and approved by the Contractor's QCO and each item shall be stamped, signed, and dated by the QCO indicating action taken.
Proposed deviations from the contract requirements shall be clearly identified along with the reason for the deviation.
The Contractor shall provide all requested Preconstruction Submittals (Generally identified in the SOW as “Submittals Required with Proposal”) at the time of proposal.
Preconstruction Submittals shall be identified in the TO SOW. Failure to provide the requested submittals will result in an unacceptable Technical Evaluation.
All material submittals and shop drawings shall be provided in digital format (e-mail or compact disc (CD)) with an AF Form 3000 attached. All AF Form 3000’s must be signed by the Contractor and shall include the TO title, project number, and TO number clearly indicated.
All drawings shall be provided in both CAD and PDF formats. All drawings shall follow Section 16, COMPUTER AIDED DRAFTING AND DESIGN (CADD)/
GEOGRAPHICAL INFORMATION SYSTEM (GIS), of the Base Facility Design Standard.
Submittals shall be legible, and shall include all technical data needed to verify that the item meets all requirements and specifications stated in the TO SOW.
All material/equipment cut sheets shall clearly identify, by prominent notation, each product or item that is being submitted upon.
21.2 [bookmark: 21.2_SCHEDULING][bookmark: _Toc230075227]SCHEDULING
Submittals covering component items forming a system or items that are interrelated shall be scheduled to be coordinated and submitted concurrently. Certifications to be submitted with the pertinent drawings shall be so scheduled. No delay damages or time extensions will be allowed for time lost in late submittals. All required submittals are identified in the TO SOW.
21.3 [bookmark: 21.3_STANDARD_PRODUCTS][bookmark: _Toc230075228]STANDARD PRODUCTS
Materials and equipment shall be standard products of a manufacturer regularly engaged in the manufacturing of such products, which are of a similar material, design and workmanship. All products shall be new unless otherwise directed in the TO SOW.
21.4 [bookmark: 21.4_SUBMITTAL_REQUIREMENTS][bookmark: _Toc230075229]SUBMITTAL REQUIREMENTS
The Contractor shall submit to the CO, all items listed or specified for each proposal within fourteen (14) working days after TO award, or as otherwise established or directed by the CO. The CO may request submittals in addition to those listed on the TO when deemed necessary to adequately describe the work covered in the respective sections.
Submittals pertinent to materials and equipment that are subject to advance approval shall be scheduled and made prior to the acquisition or the delivery thereof. Each submittal shall be complete and in sufficient detail for ready determination of compliance with the contract requirements. Submittals shall include such items as: project schedule, descriptive literature (i.e. catalog cuts, diagrams, operation charts/data); test reports; certificates of compliance; actual material sample; fabricator's drawings; shop drawings; operation and maintenance (O&M) manuals including parts lists, certifications, warranties and other such required submittals.
Indicate, by prominent notation, each product or item which is being submitted
21.4.1 [bookmark: 21.4.1_PROCEDURES_FOR_SUBMISSION][bookmark: _Toc230075230]PROCEDURES FOR SUBMISSION
The Contractor shall use AF Form 3000, Material Submittal, IAW the instructions on the reverse side thereof. This form shall be reproduced by the Contractor (the instructions on the back need not be reproduced). Special care should be exercised to ensure proper listing of the specification/drawing reference pertinent for each item submitted. All submittals shall be prepared and provided with a copy of AF Form 3000.
21.4.2 [bookmark: 21.4.2_CONTRACTOR’S_RESPONSIBILITIES][bookmark: _Toc230075231]CONTRACTOR’S RESPONSIBILITIES
Determine and verify field measurements, materials, field construction criteria; review each submittal; and check and coordinate each submittal with requirements of the work and contract documents.
Correct and resubmit submittal as directed by CO or BCE authority. When resubmitting disapproved transmittals or transmittals noted for resubmittal, the Contractor shall provide copy of that previously submitted transmittal including all reviewer comments for use by approving authority. Direct specific attention in writing or on resubmitted submittal to revisions not requested by approving authority on previous submissions.
Furnish additional copies of submittal when requested by CO, to a limit of ten
(10) copies per submittal.
The Contractor’s Quality Control Officer will certify submittals forwarded to the CO.
Ensure no work has begun until submittals for that work have been returned as "approved," or "approved as noted", except to the extent that a portion of work must be accomplished as basis of submittal.
21.4.3 [bookmark: 21.4.3_DRAWING_SUBMITTALS][bookmark: _Toc230075232]DRAWING SUBMITTALS
Project drawings shall not be less than A4 (8-1/2 by 11 inches) or more than AO (30 by 42 inches).
Present A4 (8-1/2 by 11 inches) sized shop drawings as part of the submittals required by section. Present larger drawings in sets.
21.4.4 [bookmark: 21.4.4_PRODUCT_DATA_AND_MANUFACTURER’S_I][bookmark: _Toc230075233]PRODUCT DATA AND MANUFACTURER’S INSTRUCTION
Indicate, by prominent notation, each product which is being submitted; indicate specification section number and paragraph number to which it pertains.
Submit manufacturers’ instructions prior to installation. The Contractor shall install all material and equipment IAW all manufacturer’s instructions related to the product being installed.
21.4.5 [bookmark: 21.4.5_NUMBER_OF_COPIES_OF_OPERATION_AND][bookmark: _Toc230075234]NUMBER OF COPIES OF OPERATION AND MAINTENANCE DATA
Submit one (1) copy in digital format (e-mail or CD) of O&M Data to the CO for review and approval.
21.4.6 [bookmark: 21.4.6_APPROVED_SUBMITTALS][bookmark: _Toc230075235]APPROVED SUBMITTALS
The CO's or government representative’s approval of submittals shall not be construed as a complete check but will indicate only that the general method of construction, materials, detailing and other information are satisfactory, and the design, general method of construction, materials, detailing and other information appear to meet the Solicitation and Accepted Proposal. Approval will not relieve the Contractor of their responsibility for any errors which may exist, as the Contractor under the Contractor Quality Control (CQC) requirements of this contract is responsible for design, dimensions, all design extensions, such as the design of adequate connections and details, etc. and the satisfactory construction of all work. After submittals have been approved by the CO, no resubmittal for the purpose of substituting materials or equipment will be considered unless accompanied by an explanation of why a substitution is necessary.
21.4.7 [bookmark: 21.4.7_DISAPPROVED_SUBMITTALS][bookmark: _Toc230075236]DISAPPROVED SUBMITTALS
The Contractor shall make all corrections required by the CO and promptly furnish a corrected submittal in the form and number of copies specified for the initial submittal. If the Contractor considers any correction indicated on the submittals to constitute a change to the contract, a notice IAW the Contract Clause "Changes" shall be given promptly to the CO.
21.4.8 [bookmark: 21.4.8_WITHOLDING_OF_PAYMENT][bookmark: _Toc230075237]WITHOLDING OF PAYMENT
Payment for materials incorporated in the work will not be made if required
approvals have not been obtained.
22 [bookmark: 22_PROJECT_DOCUMENTATION][bookmark: _Toc230075238]PROJECT DOCUMENTATION
TO final payment will be withheld until all close-out documents and project deliverables requested in the TO SOW have been delivered to and approved by the CO or BCE authority. Typical close-out documents and project deliverables include, but not limited to;
1. Equipment Manuals
2. Equipment Start-up Reports
3. Test & Balance Reports for HVAC Systems
4. Any Product Warranty Documents
5. As-Built Drawings, to include any Fire Alarm and Suppression System Designs, Intrusion Detection Systems (IDS) and Access Control Systems (ACS).
6. Beneficial Occupancy Document
7. Release of Claims
8. Final Contract Progress Report (AF IMT 3065)
22.1 [bookmark: 22.1_DAILY_REPORTS][bookmark: _Toc230075239]DAILY REPORTS
The Contractor shall complete and maintain a Construction Inspection record (AF IMT Form 1477), or a form acceptable to the CO, on all projects for the duration of the project. Daily Report shall be available to the CO or BCE upon request.
22.2 [bookmark: 22.2_DRAWINGS][bookmark: _Toc230075240]DRAWINGS
22.2.1 [bookmark: 22.2.1_SHOP_DRAWINGS][bookmark: _Toc230075241]SHOP DRAWINGS
(FAR 36.236-21 (d)) Shop drawings means drawings, submitted to the Government by the Contractor, subcontractor, or any lower tier subcontractor pursuant to a construction contract, showing in detail (1) the proposed fabrication and assembly of structural elements, and (2) the installation (i.e., fit and attachment details) of materials or equipment. It includes drawings, diagrams, layouts, schematics, descriptive literature, illustrations, schedules, performance and test data, and similar materials furnished by the Contractor to explain in detail specific portions of the work required by the contract. The Government may duplicate, use, and disclose in any manner and for any purpose shop drawings delivered under this contract.
Shop drawings are created prior to construction, and are agreed upon by the design team, owners, Contractors, and subs before work begins. They are not usually a part of the official contract documents, and may occasionally be produced during the course of construction as necessary.
Shop drawings; Represent building components as designed, are produced by the Contractor and subcontractors, are created after the project is awarded and before construction begins, are not usually official contract documents and may be subject to mark-ups, change orders, and redlining.
Shop Drawings shall diagrammatically show all work requested in the TO SOW.
22.2.2 [bookmark: 22.2.2_WORKING_DRAWINGS][bookmark: _Toc230075242]WORKING DRAWINGS
Shop drawings, once approved by the design team, owners, contractors and subcontractors shall become Working Drawings for use on the project.
The Contractor shall keep on the work site, a copy of the Project Working Drawings and Specifications and shall at all times provide the Air Force PM access thereto in accordance with FAR 52.236-21. Anything mentioned in the specifications and not shown on the drawings, or shown on the drawings and not mentioned in the specifications, shall be of like effect as if shown or mentioned in both. In case of a difference between drawings and specifications, the specifications shall govern. Contactor shall immediately check the furnished drawings and notify the Government of any discrepancies.
If the Contractor fails to maintain the working drawings as required herein, the CO will consider that satisfactory progress has not been achieved for the period in question.
22.2.3 [bookmark: 22.2.3_AS-BUILT_DRAWINGS][bookmark: _Toc230075243]AS-BUILT DRAWINGS
By definition, an as-built drawing is a revised set of drawings submitted by a Contractor upon completion of a construction project. As-built drawings show the dimensions, geometry, and location of all components of the project. These 2D floor plans commonly include details such as walls, doors, windows, and plumbing fixtures.
The main purpose an as-built drawing serves is to replicate how the Contractor built the project and identify what changes were made throughout the course of constructing the project.
A minimum of one set of As-Built Drawings in AutoCAD (dwg.) and PDF format must be provided on all construction and renovation projects. Drawings must be complete, accurate and comply with current Hill AFB CAD standards.
Final payment will be withheld until final as-built drawings are received and approved by the CO.
23 [bookmark: 23_EXCAVATION_(DIG)_PERMITS/WORK_CLEARAN][bookmark: _Toc230075244]EXCAVATION (DIG) PERMITS/WORK CLEARANCE (UTILITY OUTAGE) REQUEST
23.1 [bookmark: 23.1_EXCAVATION_PERMITS_(DIG_PERMIT)][bookmark: _Toc230075245]EXCAVATION PERMITS (DIG PERMIT)
The Contractor shall obtain a 75 CEG/CEOER Form 12 (Dig Permit) from the Red Stakes Office located at Building 508 for all excavation work. The Contractor will be required to mark the limits of the site work/excavation with a non-permanent White paint to indicate location, direction, length, and depth of site work/excavation in order to facilitate the utility owner’s field marking of existing utilities. Signed original permit shall be on job site during excavation.
The Contractor shall be responsible for the completion of a 75 CEG/CEOER Form 12 (Dig Permit) contacting all appropriate utility owners to coordinate work, identify, locate, and mark all utility lines in the vicinity of the project work site (commercial and military utility lines). The Contractor is responsible to maintain all utility location markings once identified and marked by utility owner.
The Contractor shall provide, as attachment to the 75 CEG/CEOER Form 12, drawings showing exact location and description of the work to be accomplished. Should any of the coordination points indicate additional utility lines or structures to those already shown on the drawings, by sketch on the Contractor’s drawing or by field location marking, the Contractor shall be responsible for the protection of each of the indicated items. It is the responsibility of the Contractor to verify the exact location of all indicated utility lines and structures, and for the protection of the same, in the project work area. Should damage occur to any utility line or structure, the Contractor shall be responsible for the prompt repair of the damage to return the item to its original working condition.
The Contractor must submit reports monthly showing the tons of material disposed of at a landfill and the tons of material diverted from a landfill.
23.2 [bookmark: 23.2_BASE_CIVIL_ENGINEER_WORK_CLEARANCE_][bookmark: _Toc230075246]BASE CIVIL ENGINEER WORK CLEARANCE REQUEST
The Contractor shall request and coordinate, all utility outages necessitated by the project work at least thirty (30) calendar days prior to the proposed outage date unless otherwise approved in writing by the CO and the 75th CES Director. Failure to do so may result in project delays and the project PoP will not be extended. Failure to perform all work during the outage time may cause a minimum of twenty-one (21) days delay due to resubmittal and approval of new outage dates. All electrical and water outages shall be performed after hours, weekends or at customer’s discretion. All outages dates shall not exceed five (5) days per outage without prior approval by SABER PM.
The Contractor shall not operate any valve, circuit breaker, or other utility shut-off device unless approved by the CO. The Contractor shall verify that there are no conflicts with the scheduled outage immediately before shutting off the utility. The Contractor shall be responsible to implement lockout/tag out procedures, as needed or required.
In all cases, the Contractor shall have contingency plans for continuing work during utility outages caused by the Contractor or outside forces. The plan must also include procedures for promptly repairing utility breaks/interruptions made or caused by the Contractor.
The Contractor shall obtain and process an AF Form 103, Base Civil Engineer Work Clearance Request (Utility Outage Request), from the 75th CES Customer Service Unit for all utility outages needed during the performance of a TO. The Contractor shall process the Utility Outage Request form for signatures and provide the Utility Outage Request form to the SABER PM for review prior to submitting the form to the CE Operation Support Flight Superintendent for signature. The Contractor shall provide a complete, approved and signed copy of the Utility Outage Request form to the SABER PM a minimum of seven (7) days prior to the scheduled outage date. The Contractor shall reference the specific TO; stipulate the specific utility system and/or circuits to be affected; any other associated buildings that may be affected; the location of the work; the time, date and duration of the requested outage for each system and describe the contingency plans for restoring the utility to service.
23.3 [bookmark: 23.3_RESTRICTIONS][bookmark: _Toc230075247]RESTRICTIONS
Outages shall be kept to a minimum both in number and in duration. When multiple outages are required, as many outages as can be accurately scheduled shall be submitted as a group. No outage shall exceed eight (8) hours unless approved in writing by the SABER PM prior to outage execution.
Unless a documented Government delay occurs, the Contractor shall be responsible for meeting outage time requirements as stated in the approved AF Form 103.
24 [bookmark: 24_TESTING_OF_MATERIALS][bookmark: _Toc230075248]TESTING OF MATERIALS
The Contractor shall follow the DoD Unified Facilities Guide Specifications (UFGS) for the testing of all materials identified in the below UFGS’;
UFGS 01-33-29	Sustainability Reporting UFGS 31-00-00	Earthwork
UFGS 32-11-20	Base Course for Rigid and Subbases for Flexible Paving UFGS 32-12-16	Hot Mix Asphalt (HMA) for Roads
UFGS 32-13-13.06	Portland Cement Concrete Pavement for Roads and Site Facilities UFGS 32-13-14.13	Concrete Paving for Airfields and Other Heavy Duty Pavements UFGS 32-16-19	Concrete Curbs, Gutters and Sidewalks
UFGS 31-17-23	Pavement Markings UFGS 33-40-00	Storm Drainage Utilities

The Contractor shall follow all MSDS directions to ensure workers and work area are protected from fire and health hazards resulting from the handling, mixing and application of paints used.
All material or system tests that are charged as a direct TO expense shall be certified and submitted in the original form. The Contractor shall notify both the SABER PM and the CO at least twenty-four (24) hours prior to conducting tests.
Concrete compressive strength test cylinders or borings shall be taken in the presence of, and as directed by the SABER PM. The Contractor shall notify both the CO and the SABER PM at least twenty-four (24) hours prior to placement of any concrete. The Contractor shall label all test cylinders immediately with black permanent marker clearly identifying the cylinder number, project number, and date. Cylinders shall remain on the project site until they are tested.
Compaction tests of fill material shall be performed in the presence of the SABER PM, who will specify the location where each test is to be taken. Compaction tests are required for each lift.
The Contractor shall notify both the CO and the SABER PM of the scheduled time and date for testing each lift at least twenty-four (24) hours in advance. Any compaction test performed without the SABER PM present will not be accepted.
When heating up an area for concrete placement or curing, propane and/or gas heaters shall not be used as it can cause carbonation within the concrete.
25 [bookmark: 25_PRE-FINAL_AND_FINAL_INSPECTIONS][bookmark: _Toc230075249]PRE-FINAL AND FINAL INSPECTIONS
The Contractor shall schedule and hold Pre-Final and Final inspections for each TO. The inspections will be conducted by the customer, SABER PM, CO, Prime Contractor and subcontractors.
The Contractor’s QCO shall perform an inspection of the project and project area prior to the pre-final inspection and provide their punch list to the SABER PM at the time of the pre-final inspection.
The Contractor shall schedule a pre-final inspection a minimum of seven (7) days prior to the PoP completion date to conduct a pre-inspection of the project. The Contractor shall have seven
(7) days to complete all punch list items and any other items that are part of the project.
The Contractor shall have all punch list items, any other items that are part of the project and final cleaning of the project area complete at time of final inspection. The Contractor shall provide all requested/required project deliverables and close-out documentation at time of final inspection. Full Beneficial Occupancy or final Contract Progress Report will not be accepted until all parts of the project are completed to the satisfaction of the CO, SABER PM and customer and all project deliverables are provided and accepted.
26 [bookmark: 26_WARRANTY][bookmark: _Toc230075250]WARRANTY
The Contractor shall provide a minimum one-year warranty on all work in accordance with FAR 52.246-21, Warranty of Construction. The CO shall notify the CM of warranty issues. After being notified of a problem, the Contractor must respond within 24 hours and investigate and/or resolve the issue(s). If the CM believes the issue is not warranty related, he may request a fact-finding visit with the CO and SABER PM. If the fact-finding meeting determines the issue is warranty related, the Contractor must repair the item within forty-eight (48) hours, or as determined by the CO.
The Prime Contractor is responsible for ensuring subcontractors fulfill warranty requirements on their work. Manufacturer warranties for all material and equipment installed under an individual TO, shall be submitted to the CO with an AF Form 3000 prior to closeout.
If warranty or repair work is not sufficient or does not correct the issue(s), the Contractor shall return as often as needed to resolve the issue(s). If any issues have not been resolved for any reason at the end of the warranty period, the Contractor shall extend the warranty period for one additional year to cover any work, design or re-design, equipment or system changes needed to resolve any warranty issues.
If multiple warranty issues occur for the same item/issue and are not resolved to the satisfaction of the CO, the Contractor shall extend the warranty for one (1) year from date of last repair.
27 [bookmark: 27_CONTRACTOR’S_AS-BUILT_DRAWINGS][bookmark: _Toc230075251]CONTRACTOR’S AS-BUILT DRAWINGS
During the progress of the work, the Contractor shall keep a careful record at the job site of all changes and corrections from the layouts shown on the Working Drawings. The Contractor shall enter such changes and corrections on As-Built Drawings promptly. The As-Built Drawings shall also indicate the actual location of all subsurface utility lines encountered, including each change in direction by offset dimensions to two permanently fixed surface features. Valves, splice boxes, etc. shall be located by dimensioning along the utility run from a reference point.
The depth below the surface of each run shall also be recorded. Upon construction completion, the Contractor shall submit to the CO one copy of as-built hard copy prints and the set of drawing files showing the aforementioned data. The Contractor shall also submit the same documents digitally through e-mail, compact disc or via the secure web-based document share site. The red-lined record drawings must be available for review. Final acceptance of a TO will not be issued until all as-built drawings and O&M manuals are received and approved.
Contractors should take this into consideration when determining the PoP for each TO. As-Built CADD Requirements
1) All drawing files shall be created using the Computer Aided Design and Drafting (CADD) software.
2) The Contractor will use vector elements to construct all portions of the electronic drawings. Raster elements are only authorized to show pre-construction conditions.
3) The Contractor shall furnish one drawing file for each drawing sheet submitted. Multiple drawing sheets per drawing file will not be accepted.
4) The Contractor shall submit one set of media containing the computer drawing files for each project.
5) In general, the Contractor shall provide all data necessary to display, edit, and plot the files produced for each project.
6) The as-built files shall be clearly labeled with the drawing number or content, project name and number.
Before a CADD file is submitted, the following procedures shall be performed
1) Remove all extraneous graphics outside the drawing border area.
2) Ensure all layers required to properly plot the respective drawing are activated or deactivated accordingly.
3) Make sure reference files are attached without device or directory specifications (x-refs shall load properly from any electronic storage area).
4) All drawing files must be capable of being saved and opened using the “DWG” extension.
28 [bookmark: 28_GOVERNMENT_FURNISHED_EQUIPMENT/MATERI][bookmark: _Toc230075252]GOVERNMENT FURNISHED EQUIPMENT/MATERIALS/PROPERTY
The Contractor, with his own forces, shall transport all government-furnished equipment (GFE) and/or government-furnished materials (GFM) and/or government-furnished property (GFP), if applicable, as described on the TO. The GFE/GFM/GFP shall be transported from the government’s storage area to the work site or as indicated on the TO. The Contractor shall follow the instructions of the CO regarding the disposition. GFE/GFM/GFP will be determined at the TO level.
29 [bookmark: 29_SCHEDULING_WORK][bookmark: _Toc230075253]SCHEDULING WORK
Each TO shall be diligently worked according to the progress schedule and without extending performance periods due to insufficient resources.
Prior to beginning any individual TO construction activities, the Prime Contractor shall coordinate with the CO and SABER PM and schedule a Pre-Construction meeting between the CO, Prime Contractor, Subcontractors, SABER PM and Customer a minimum of two (2) weeks prior to the NTP project start date. Topics of discussion may include; a detailed review of the project requirements, contractor vehicle and equipment parking, access to the building and work area, delivery of materials, space for storage of materials and equipment, use of approaches, corridors, stairways and elevators, safety and control of building occupants, overhead work, use and placement of cranes, scheduling concerns, project documentation requirements i.e., crane waivers, outage or dig permits, hot work permits, etc., and any other pertinent information related to the project.
Project Phasing - When specifically requested by the Government in the TO SOW, the work shall, so far as practicable, be done in definite sections or areas and confined to limited areas that shall be completed before working in other areas. These areas shall be clearly annotated on the Contractor’s construction drawings.
30 [bookmark: 30_WORK_IN_OCCUPIED_AREAS][bookmark: _Toc230075254]WORK IN OCCUPIED AREAS
The Contractor shall perform all work in a manner which will minimize disruptions to normal Hill AFB operations.
The Contractor shall protect all routes from damage or wear and shall repair all areas to provide an undisturbed appearance.
Only route(s) designated by the CE team for each TO shall be utilized by the Contractor for access to the work site. The use of an existing elevator shall be arranged prior to use through the CE team and subject to their controls. Such use will be of an intermittent and temporary nature. The Contractor shall provide and maintain suitable and adequate protective covering for the elevator machinery, the hatchway entrance, and the interior of elevator during any period of temporary usage. In no case shall the load exceed the rated capacity of the elevator.
The Contractor will be allowed a reasonable working area.
The Contractor shall comply with all applicable Hill AFB policies and regulations pertaining to safety, health, security, traffic control, fire prevention, and environmental protection.
All laydown areas shall be brought back to their original condition and provide undisturbed appearance.
31 [bookmark: 31_COORDINATING_WITH_GOVERNMENT_ACTIVITI][bookmark: _Toc230075255]COORDINATING WITH GOVERNMENT ACTIVITIES
Construction work closely related to and/or located at the site of the work under this contract, including other military projects and normal maintenance and repair work may occur. The Government reserves the right to engage in and to perform work, with its own forces or other contractor forces, of the same type as the successful contractor without breaching or violating this contract.
32 [bookmark: 32_NOISE_AND_EMMISSION_CONTROL_OF_EQUIPM][bookmark: _Toc230075256]NOISE AND EMMISSION CONTROL OF EQUIPMENT
All equipment utilized by the Contractor that produces noise levels in excess of 84 DBA (“A” weighted decibels) must be so identified by the Contractor. This equipment shall be utilized in a manner that prevents exposure of the occupants or any persons other than contractor personnel to levels exceeding 84 DBA. This may cause night or weekend work and will not be considered as a change order to the project scope if the time of use of such equipment is not provided in the TO SOW or requested by the Contractor at time of RFI submission.
The Contractor shall not play radios or other audio equipment at levels that allow sounds to be heard outside the immediate work area. Songs or lyrics shall not be of a derogatory, disgraceful or racial nature. Any request to reduce or turn the audio equipment off shall be fulfilled.
All power equipment utilized by the Contractor that produces exhaust fumes shall only be operated in a negative pressure environment, regardless of building occupancy or time of day. All exhaust fumes shall be captured and released outside. This may cause night or weekend work and will not be considered as a change order to the project scope if the time of use of such equipment is not provided in the TO SOW or requested by the Contractor at time of RFI submission.
33 [bookmark: 33_CONSTRUCTION_SITE_MAINTENANCE][bookmark: _Toc230075257]CONSTRUCTION SITE MAINTENANCE
Hallways, exits and access routes must be kept free of debris and safe at all times. Prior to departure from the work area each day, the Contractor shall remove and properly dispose of all waste materials or rubbish generated by the project work in a contractor supplied dumpster/trailer. The Contractor shall not use government dumpsters for construction debris/material. Daily cleanup of all job sites includes leaving the affected project area in a good state of order. Thorough daily cleanup may be required in certain high-visibility areas on a case-by-case basis as described in the project SOW for specific TOs. Upon completion of the project, the Contractor shall conduct a thorough final cleaning.
All chutes used for refuse, and the like, shall be covered or of such design to fully confine the material to prevent the dissemination of dust.
All materials removed and not reused on the project as specified herein or as required by the project SOW, drawings, or specifications, remain the property of the Government. The CO will determine if these materials are salvageable or unsalvageable. Salvageable materials shall be managed as directed by the CO with the concurrence of the Installation Environmental Office.
Unsalvageable materials, as determined by the CO, shall become the property of the Contractor and disposed of at the Contractor's expense. Materials to be removed shall be removed without damage to adjacent areas. All damage resulting from the removal activity shall be repaired by the Contractor at no cost to the Government. Repair shall be made with materials of like nature, type and construction as those which were damaged or as those which exist adjacent to the areas to be repaired.
34 [bookmark: 34_BASE_UTILITY_SERVICES][bookmark: _Toc230075258]BASE UTILITY SERVICES
All reasonably required amounts of water and electricity, where available, will be made available to the Contractor by the Government from existing system outlets and supplies. The quality, quantity and consistency of the utilities supplied are not guaranteed. Some TOs may not allow the use of government utilities. The Contractor shall, at his own expense, make all temporary connections and install distribution lines. Temporary connections to the base water or electrical supply shall be approved by the utility owner. All temporary lines shall be installed and maintained by the Contractor in a safe and working manner subject to approval by the CO and Utility Owner and shall be removed by the Contractor in like manner prior to final acceptance of the construction. Reasonable quantities of electricity and water used to make final tests of completely installed systems will be furnished by the Government as determined by the CO prior to execution.
Only compatible adapters shall be utilized for hydrant connections. All connections to fire hydrants shall be provided with a backflow preventer. A hydrant wrench of the correct size shall be used to control the flow. Temporary connections to fire hydrants shall be disconnected at the end of each working day. Any use of fire hydrants shall be coordinated with and approved by the Hill AFB Fire Department & American Water prior to work. Notification by the Contractor to the CO, Hill AFB Fire Department, and American Water shall be made at least ten (10) workdays prior to any connection.
35 [bookmark: 35_PRIVATIZED_UTILITIES][bookmark: _Toc230075259]PRIVATIZED UTILITIES
35.1 [bookmark: 35.1_AMERICAN_WATER][bookmark: _Toc230075260]AMERICAN WATER
On September 1st, 2014, American Water (AW) began Contract SP0600-14-C-8290. Section C 11 of this contract dictates the interaction of AW with third party contractors performing construction at Hill AFB. Because many third-party construction projects were already underway before September 1st, 2014, adjustments to AW’s third-party construction protocol were necessary to accommodate transition. This document serves as clarification of and guidance for AW’s protocol for third party projects beginning construction after January 1, 2015.
[bookmark: _Toc230075261]Connections and Disconnections:
According to Section C.11.3 of the Contract, AW is responsible for the addition/deletion of service points to AW’s system. AW will be reimbursed for its efforts as follows:
Temporary Connections: The Government will identify the party responsible to reimburse AW for temporary connections. The responsible party (Contractor) will provide AW with the following information:
1) Name of Responsible Party’s Representative
2) Cost
3) Date of Installation
4) Expected duration of the connection
5) Description of the connection, including route and type of material
6) POC, Title, and Phone Number
Upon receipt of this information, AW will provide the Contractor with a cost estimate for AW’s services and will coordinate services with the responsible party’s representative. The Contractor retains responsibility for necessary dig and outage permits according to established Hill AFB protocol.
Permanent Connections: The Government will identify the party responsible (Contractor) to reimburse AW for permanent connections and associated construction/system adaptation. The Contractor will provide AW with the project design as early as possible. Upon receipt of this information, AW will submit a detailed proposal identifying the work necessary to provide the required utility services, any proposed connection charge, and the proposed change in the monthly utility services fee that will go into effect upon completion and placement into service of the new connecting facilities. AW will submit this to the Government, upon approval from the Government, AW will coordinate services with the responsible party’s representative. The Contractor retains responsibility for necessary dig and outage permits according to established Hill AFB protocol.
[bookmark: _Toc230075262]Third Party Construction:
Where the Government contracts with a third party to construct new infrastructure that is intended to connect with AW’s system, AW will provide the Government and the third party with AW’s Specifications. The Government will require the third party to meet AW’s Specifications for infrastructure that will connect to AW’s system. AW will provide a review of completed construction plans when plans are submitted to AW. The Government shall require bidders for third party construction to solicit a bid from AW for the portion of the work intended to connect to AW’s system. Bid solicitations shall be sent to the Contractor. If AW is selected, the work will be performed to AW specifications by AW personnel and contractors. AW will take ownership of the improvements.
If AW is not the successful bidder on a project including infrastructure intended to connect to AW’s system, AW shall have the right to reasonably inspect the third party’s construction of components for which AW is intended to take ownership. The Contractor shall pay for inspection and connection services and all fees or cost should be include in the Contractor’s quote to the government. If the third party constructed components are not in compliance with AW specifications, AW will specify what is out of compliance to the Government and Contractor. The Government may direct the third party or AW to correct deficiencies. If AW corrects the deficiencies, AW will be compensated by the Contractor according to agreed-upon project scope and price.
35.2 [bookmark: 35.2_CITY,_LIGHT,_&_POWER][bookmark: _Toc230075263]CITY, LIGHT, & POWER
Hill Air Force Base’s electrical distribution grid has been “privatized” – conveyed to a non-governmental system owner City Light and Power (CLP). CLP is the owner and operator of grid and may be viewed just like any other local utility. The most common point of demarcation, i.e. where the government assumes ownership, is at the secondary terminals of a transformer. The transformer itself, along with infrastructure carrying voltages higher than 600 volts, typically belongs to CLP. For the purposes of this document, “medium voltage” shall refer to voltages greater than 600 volts.
CLP requires all new electrical connections and equipment to comply with their specifications in order to protect the integrity of their electrical distribution system. The government CO’s preferred method is for CLP to do all electrical work up to the point of demarcation to include procurement of, placement of, and connection of the primary terminations to the transformer.
No medium voltage work will be performed by any entity other than CLP. Regardless of who installs electrical equipment, final connections to Hill AFB electrical distribution system must be made by CLP. The CLP team will also perform follow-up inspections and service.
There will be an inspection and/or connection fee associated with CLP efforts. Requests for connections, inspections, or quotes will be presented to CLP using a form supplied by CLP. CLP points of contact include:
Rich Houghton Installation Manager 801-660-2255
rhh@clpinc.com

Todd Cook Crew Supervisor 801-660-2255
tjc@clpinc.com

Any fees or cost charged by CLP shall be the responsibility of the Contractor, not the government, and should be included in Contractor’s quote to the government.
36 [bookmark: 36_ENERGY_CONSERVATION/MANAGEMENT][bookmark: _Toc230075264]ENERGY CONSERVATION/MANAGEMENT
The Contractor shall follow all requirements outlined in the most recent version of the Base Facility Design Standard.
The Contractor shall be responsible for operating under conditions that preclude the waste of utilities and shall comply with energy conservation directives for each installation.
Supplemental lighting shall be used only in areas where and when work is actually being performed. When work areas are vacated, lighting shall be turned off.
Mechanical equipment for heating, ventilation, and air conditioning systems shall be adjusted by authorized craftsman only.
Water faucets or valves shall be turned off after the required usage has been accomplished.
37 [bookmark: 37_SANITARY_PROVISIONS][bookmark: _Toc230075265]SANITARY PROVISIONS
Use of government facilities may not be allowed. The Contractor shall utilize only those restrooms designated for their use, provided such usage does not conflict with usage by installation personnel and that such usage does not result in unsanitary conditions or damage to the restroom. If government restrooms are authorized as part of a TO, the Contractor will be required to maintain standard cleanliness in restrooms during the project and perform a thorough cleaning of the restrooms prior to final inspection. Should usage by the Contractor result in unsatisfactory conditions, the CO may restrict or prohibit further usage by the Contractor. In no instance shall paint or other construction materials be disposed of in the rest room sanitary sewer drains nor shall fixtures be utilized for cleaning tools or construction equipment. If construction debris is found in the facilities sanitary sewer system, the Contractor shall be required to video the drain system and remove any blockages associated with the debris and return the drain system to a fully operational state.
The Government, at its discretion, may direct the Contractor to provide temporary toilets for the Contractor’s use. When the Contractor provides their own temporary toilets, they shall ensure that they satisfy state and local health requirements for the use of construction personnel.
Location, type, proposed maintenance to include dumping and sanitizing, etc., shall be approved by the CO prior to placing toilets. Temporary toilets shall be promptly removed at the completion of construction. All costs incurred in connection with the temporary toilets shall be borne by the Contractor.
38 [bookmark: 38_CONTRACTOR_VEHICLES/PARKING][bookmark: _Toc230075266]CONTRACTOR VEHICLES/PARKING
The company name shall be prominently and noticeably displayed on both sides of all Contractor vehicles and equipment operated on Hill AFB. The Contractor may obtain temporary vehicle entry passes needed to transport materials and equipment at Building 1964, (Truck Gate). The Contractor shall be equipped to present proof of insurance, driver’s license, vehicle registration, and any other documentation required to obtain a vehicle pass. Entry to the restricted area of Hill AFB will require a vehicle pass and additional clearances (i.e. for personnel) as described in Security Requirements for Hill AFB, below.
39 [bookmark: 39_TRANSPORTATION_OF_CONSTRUCTION_EQUIPM][bookmark: _Toc230075267]TRANSPORTATION OF CONSTRUCTION EQUIPMENT
Delivery of materials and equipment shall be made with a minimum of interference to government operations and personnel.
If road closures are necessary for the transportation or operation of equipment, the Contractor is responsible for submitting a road closure request on AF Form 103, Base Civil Engineer Work Clearance Request (Utility Outage Request) a minimum of thirty (30) days prior to closure date.
40 [bookmark: 40_HILL_AFB_SPECIFIC_TRAINING][bookmark: _Toc230075268]HILL AFB SPECIFIC TRAINING
Hot Work
1) All Prime Contractor employees or subcontractors employees performing any “Hot Work” are required to attend a Hot Work (Burn) Permit class prior to performing any hot work on Hill AFB and each year thereafter (annual requirement). Any cost or time associated with obtaining certification shall be at the Contractor’s expense.
2) Hot work includes, but not limited to, any/all; welding, cutting, soldering, brazing, grinding and any work that produces sparks.
3) Classes are held the 1st Thursday of each month at Building 23 (Main Fire Station) 1st Floor Training Room. Enter main entry, first right. Contact the F.D. at 777-3021 for additional information.
4) Any Prime Contractor employee or subcontractor employee performing hot work shall have a current Hot Work Certificate available anytime hot work is being performed and provide certificate upon request by the Government. If a Prime Contractor employee or subcontractor employee is unable to provide certificate upon request, the Prime Contractor will be notified with a request for corrective action. The Prime Contractor employee or subcontractor employee will be removed from the job site until such certification is obtained and presented to the CO.
[bookmark: _Toc230075269]Confined Space
1) Any Contractor employee requiring entry into a confined space shall follow all confined space requirements identified in DAFMAN 91-203, Chapter 23 and shall accomplish all training that aligns with OSHA requirements.
[bookmark: _Toc230075270]Annual Asbestos Training.
1) The Contractor shall provide annual asbestos training IAW OSHA Occupational Safety and Health Standards 1910.1001(j)(7), specifically 1910.1001(j)(7)(iv); The employer shall also provide, at no cost to employees who perform housekeeping operations in an area which contains ACM or PACM, an asbestos awareness training course, which shall at a minimum contain the following elements: health effects of asbestos, locations of ACM and PACM in the building/facility, recognition of ACM and PACM damage and deterioration, requirements in this standard relating to housekeeping, and proper response to fiber release episodes, to all employees who perform housekeeping work in areas where ACM and/or PACM is present. Each such employee shall be so trained at least once a year.
41 [bookmark: 41_SECURITY_REQUIREMENTS_FOR_HILL_AIR_FO][bookmark: _Toc230075271]SECURITY REQUIREMENTS FOR HILL AIR FORCE BASE
The Contractor shall conform to base regulations and directives pertaining to security, safety, fire, traffic and personnel clearances while on Hill AFB.
41.1 [bookmark: 41.1_LONG-TERM_PASSES_(DBIDS_CARD)][bookmark: _Toc230075272]LONG-TERM PASSES (DBIDS CARD)
Passes for longer than 120 days may be picked up at Building 430, Security Forces Pass & ID, after the employee has been notified that the local files check has been completed during normal duty hours (0700 to 1600) by each individual with proper picture identification, proof of current insurance and registration for each vehicle. The Contractor is responsible for requesting access to the base for their personnel by completing and submitting AF Form 496 to the CO, or their representative, at AFSC OL: H/PZIOC.
Long-term passes will be issued to the contract on-site staff. Information requirements are as follows:
1) Be in writing on company letterhead.
2) Be certified by an authorized representative of the prime Contractor that the specified individual(s)/vehicles require access to the base and will work on the SABER project identified.
3) Specify the Contract Number.
4) Identify the specific company, (i.e. Contractor, subcontractor, supplier) covered by the request (NOTE each subcontractor request shall be separately submitted).
5) Specify the period of time when access will be required.
6) Identify specific personnel/vehicle information.
7) Provide the full name of each individual, including middle name and suffixes (e.g. Jr., III, etc.) Do not list aliases, nicknames, etc.
8) Provide each individual's driver's license number and state where issued.
41.2 [bookmark: 41.2_SHORT-TERM_PASSES][bookmark: _Toc230075273]SHORT-TERM PASSES
Short-term passes are arranged through the CO by providing the name of the Contractor, the Contractor’s driver’s license number and state of issue. The CO will enter the Contractor’s information into the 75 SFS Visitor Control website at least three (3) days prior to the Contractor’s arrival for a local files check. When the local files check is complete, the CO will notify the Contractor that they can proceed to the Hill AFB South Gate visitor center to get their entry credentials. The Contractor will need to have photo identification as well as a current driver’s license, registration and proof of insurance if they intend to operate a vehicle on Hill AFB.
41.3 [bookmark: 41.3_UNAUTHORIZED_ACTIVITY][bookmark: _Toc230075274]UNAUTHORIZED ACTIVITY
The Contractor shall inform all personnel working under his/her jurisdiction (including subcontractor and supplier personnel) that access to areas outside of the immediate work area (excluding cafeterias and restroom near the work site, direct haul and access routes, Contracting and Civil Engineering offices and points of supply and storage) is prohibited.
Circulation of said personnel will be limited to official business only. Persons engaged in unauthorized reconnaissance of other contractor or Government activity will be referred to the CO for disposition. Infractions involving possible compromise of national security will be turned over to the FBI for disposition and may result in termination of the contract.
41.4 [bookmark: 41.4_DENIAL_OF_BASE_ACCESS][bookmark: _Toc230075275]DENIAL OF BASE ACCESS
Access to the installation and controlled areas can be denied based on criminal history and outstanding warrants. If Contractor personnel are not granted access to the installation based on criminal history and/or outstanding wants and warrants, the contractor may be assessed liquidated damages IAW FAR 52-211-12 for any resultant schedule delay.
41.5 [bookmark: 41.5_OPERATIONAL_DELAYS][bookmark: _Toc230075276]OPERATIONAL DELAYS
The Contractor personnel shall leave Hill AFB upon notification by the CO or constituted authority when directed that operational requirements or emergencies dictate. Official snow call or late reporting may affect the Contractor’s production for which the CO will not consider reimbursement for lost work time. Normal delay should not exceed one hour in duration, but may.
41.6 [bookmark: 41.6_HILL_AIR_FORCE_BASE_SECURITY][bookmark: _Toc230075277]HILL AIR FORCE BASE SECURITY
41.6.1 [bookmark: 41.6.1_SECURE/RESTRICTED/CONTROLLED_AREA]SECURE/RESTRICTED/CONTROLLED AREAS
Hill AFB is a closed base. Within the installation boundary, there are permanent Restricted and Controlled areas. Restricted means, by definition, contain priority resources and are established pursuant to Department of Defense (DoD) Directive 5200.8, Security of DoD Installations and Resources. Because priority resources are contained within the restricted area, a single security system and circulation controls are required.
41.6.2 [bookmark: 41.6.2_RESTRICTED_AND_CONTROLLED_AREA_AC][bookmark: _Toc230075278]RESTRICTED AND CONTROLLED AREA ACCESS
Controlled/Restricted area badges are controlled items. There must be a legitimate need for a Contractor to have a controlled/restricted area badge beyond simple convenience. A Contractor must demonstrate that they will require unescorted access to a controlled/restricted area at least 3-5 times per week for at least six (6) months and that the Contractor has met the security requirements specific for the area they require access to. The Contractor is responsible for requesting access to Controlled and Restricted Areas before base entry credentials are requested. Regular, unescorted access to a Controlled area on Hill AFB requires issuance of a DBIDS card and a Controlled Area Badge. A background check of each individual requesting unescorted entry to a controlled area will be made before access is authorized. As the local files check for Hill AFB long term passes (DBIDS cards) is the same for controlled area badge issuance, the AFMC Form 496 for a DBIDS card should be sent through the 75 CEG Group Security Manager to avoid duplicate local files checks. The 75 CEG Security Manager is currently located in Building 593 North, Room 120
The Government may require that the Contractor be under Government escort during performance of a project within a Controlled or Restricted area. Warning signs mark Controlled or Restricted areas. Controlled areas contain valuable resources and are clearly marked with a “Controlled Area” sign. Restricted areas contain priority resources and are clearly marked with a “Restricted Area” sign. All personnel must obtain specific written permission to enter restricted areas. Work in some areas of the base may require special briefings for the Contractor’s employees (special briefings are required before any work is accomplished within the flight line area).
Personnel and equipment entry may be subject to delays due to security processing. The Contractor shall not be compensated for reasonable delays in accessing the site. Due to the nature of controlled and restricted areas, the Contractor may be requested to leave the area at any given time. The CO may extend the contract performance time when area designations change while the Contractor is working.
Processing Time: The above information shall be submitted to the CO a minimum of fifteen (15) calendar days, or thirty (30) calendar days for access to secure/restricted areas, in advance of when access to the job site will be required.
41.6.3 [bookmark: 41.6.3_CIRCULATION_CONTROL][bookmark: _Toc230075279]CIRCULATION CONTROL
Restricted Area Badge for Unescorted Entry only (i.e. not requiring or authorized access to classified information) may be issued to Contractor personnel meeting the following qualifications:
Subject will be employed for six (6) or more months. Contract is for more than six (6) months.
Subject’s company has at least initiated a National Agency Check with Local Agency Check (NACLAC) for adjudication of a Secret security clearance.
Subject has received a favorable local agency/files check initiated by 75 SFS.
1) NOTE: Badges authorized under the aforementioned provisions are only for areas on Hill AFB. No other areas, restricted or controlled, will be entered on the badge. Badges will not be electronically coded for any module or controlled by the Advance Entry Control System (AECS), nor will the individual be granted escort authority. If any other areas are required, the badge will be issued only upon completion of the National Agency Check (NAC).
Security Forces personnel will verify the identity and authorization of each Contractor employee requesting entry to the installation or restricted area, and may conduct searches of any hand-carried item, container, or vehicle used by the Contractor under this contract.
The contractor shall absorb all costs associated with delays at the installation entry points, restricted area entry points, or any other locations affected by security entry/circulation control measures.
41.6.4 [bookmark: 41.6.4_CONTRACTOR_VEHICLES][bookmark: _Toc230075280]CONTRACTOR VEHICLES
The Contractor will be required to present proof of insurance, driver’s license, vehicle registration, and other documentation as needed to operate a vehicle on Hill AFB. The company name shall be prominently and noticeably displayed on both sides of all vehicles operated on Hill AFB.
41.6.5 [bookmark: 41.6.5_INFORMATION_ACCESS][bookmark: _Toc230075281]INFORMATION ACCESS
Contractor access to classified information is prohibited. When Contractor performance occurs within restricted or controlled areas, or within close physical proximity of classified information, Contractor compliance with various levels of security instructions is required.
41.6.6 [bookmark: 41.6.6_GOVERNMENT_PROJECT_MANAGER_(GPM)][bookmark: _Toc230075282]GOVERNMENT PROJECT MANAGER (GPM)
The GPM will attempt to resolve security issues/problems between the Contractor and Security Forces depending on the nature of the security issue.
The Contractor shall follow and obey all laws while on Hill AFB.
41.6.7 [bookmark: 41.6.7_COMMUNICATIONS_SECURITY_(COMSEC)_][bookmark: _Toc230075283]COMMUNICATIONS SECURITY (COMSEC) MONITORING
In accordance with Air Force Instruction 33-211, all communications with DOD organizations are subject to communications security (COMSEC) review.
Contractor personnel will be aware telephone communications networks are continually subject to intercept by unfriendly intelligence organizations. The DOD has authorized the military departments to conduct COMSEC monitoring and recording of telephone calls originating from, or terminating at DOD organizations. Therefore, civilian Contractor personnel are advised any time they place a call to, or receive a call from a USAF organization, they are subject to COMSEC procedures. The Contractor will assume the responsibility for ensuring wide and frequent dissemination of the above information to all employees.
41.6.8 [bookmark: 41.6.8_FREE_ZONES][bookmark: _Toc230075284]FREE ZONES
Free zones are created inside restricted and controlled areas when construction projects make normal circulation controls inappropriate. When possible, the Contractor will create a free zone corridor between the restricted and controlled areas entry control point and the project location. If a safe corridor is not possible, government project customer will escort Contractor personnel to and from the project location. Projects requiring a free zone shall be coordinated with the SABER PM at the time of project award.
41.6.9 [bookmark: 41.6.9_RIGHT_TO_DENY_ENTRY][bookmark: _Toc230075285]RIGHT TO DENY ENTRY
The Installation Commander or designated representative reserves the right to deny entry to any Contractor whose NAC is unfavorable, and the right to terminate the entry authorization of any Contractor employee upon disclosure of information which indicates the individual’s continued entry onto Hill AFB is not in the best interest of national security. Additionally, the violation of any deviation from established security procedures by the Contractor’s employee may result in the confiscation of all access credentials and the denial of future entry onto Hill AFB.
41.6.10 [bookmark: 41.6.10__RECORDING_DEVICES][bookmark: _Toc230075286]RECORDING DEVICES
Cameras, PDA’s, Blackberry’s, Cell Phones, Smart Watches, key FOB’s or any other recording devices shall not be allowed in Restricted Areas (RA’s) or Sensitive Compartmented Information Facility (SCIF) areas.
42 [bookmark: 42_SPECIAL_PROVISIONS_FOR_WORKING_ON_OR_][bookmark: _Toc230075287]SPECIAL PROVISIONS FOR WORKING ON OR NEAR THE AIRFIELD OR AIRFIELD HANGARS
The following provisions apply when work is required to take place on an active airfield/hangar, or within the clear zones or primary surfaces. Flight lines are present on Hill AFB. If the Contractor is required to drive on the flight line; they must receive the required license and training in accordance with AFI 13-213 Airfield Driving.
All runway, taxiway or hangar closures will require the coordination with Airfield Management through the CO not less than thirty (30) calendar days prior to the requested closure, unless otherwise provided for in these specifications. The Contractor will make the maximum utilization of time during the requested closure period. The Contractor will notify the CO when he is finished with the work requiring the closure. The Contractor will schedule operations in phases if necessary so as to minimize the effect of construction closures on normal airfield operations.
The Contractor shall coordinate with the CO before initiating any work and will notify them of the proposed location of work and time of operation.
Aircraft and support equipment operating in/near hangars, on/near the runways, taxiways, and aprons make the area of construction a zone of high level noise. The Contractor shall take the necessary precautions, such as the use of earplugs or muffs to prevent injury to the auditory systems of all personnel working in the area.
42.1 [bookmark: 42.1_RESTRICTIONS][bookmark: _Toc230075288]RESTRICTIONS
No Contractor vehicles, equipment, or personnel shall be on or crossing any active runway or taxiway, except during construction period closures as outlined herein or when clearance is requested from and granted by the control tower. All Contractor vehicles operating on the landing areas (1,000 feet on either side of the runway center line) during the period from dawn to dusk will be identified by mounted electric battery operated low intensity, yellow or amber flashing lights. When Contractor operations require them to cross an active runway or other controlled area on a regular basis, they shall furnish a two-way radio in order to maintain contact with the control tower. The Government will provide the Contractor with the correct frequency. Use of the government provided radio frequency for other purposes is strictly prohibited.
42.2 [bookmark: 42.2_CLEANLINESS_OF_WORK_AREA][bookmark: _Toc230075289]CLEANLINESS OF WORK AREA
The Contractor will be required to maintain cleanliness of all work areas at all times during progression of work in order to alleviate foreign object damage (FOD). The Contractor will be required to remove all materials and equipment to a safe distance from the runway or aircraft parking area at the close of each day’s work. This distance will be determined by the Airfield Manager. The Contractor will not be allowed to stockpile any materials or store any equipment within 1,000 feet of the runway centerline.
42.3 [bookmark: 42.3_EMERGENCIES][bookmark: _Toc230075290]EMERGENCIES
There may be periods of time depending on the area you are working when the Contractor, due to declared aircraft emergencies or DEMO flights, will be required to vacate the work site and move their personnel and equipment a distance of several hundred feet away from the work site. Such removals, when ordered, will be given on short notice and expeditious action will be required. Whenever the Contractor is required to clear the work area, the Contractor accompanied by the inspector or Air Force representative will make an inspection sweep of the entire area to ensure all tools, equipment, and personnel have been removed from the runway, active taxiway or hangar, and that the area is available for landings or parking.
43 [bookmark: 43_WORKING_IN_SPECIAL_SECURITY_AREAS][bookmark: _Toc230075291]WORKING IN SPECIAL SECURITY AREAS
Many buildings on Hill AFB have special security requirements that require all personnel working on the project to be U.S. Citizens. The Contractor shall ensure that any project that references Department of Defense Manual (DoDM) 5200.01 or Intelligence Community Directive 705 (ICD-705) (Sensitive Compartmented Information Facilities), ICS 705-1, and/or ICS 705-2 (Standards for Accreditation and Reciprocal Use of Sensitive Compartmented Information Facilities) have only U.S. Citizens working them. The Contractor shall submit any/all information requested for proper vetting of Contractor employees. The government issued TO SOW shall identify all information required from Contractor employees.
43.1 [bookmark: 43.1_UTAH_TEST_&_TRAINING_RANGE_(UTTR)_A][bookmark: _Toc230075292]UTAH TEST & TRAINING RANGE (UTTR) ACCESS REQUIREMENTS
The UTTR requires specific access. The Contractor will be required to complete Hill AFB Form 0-74, Visit Request/Authorization, Attachment #5, for all employees and subcontractors necessary to perform work. Upon completion of the form, forward to the CO for coordination, See paragraph A-817 of Hill AFB Form 0-74, Visit Request/Authorization, Attachment #5 for specific requirements. Where a conflict exists, the procedures in AFI 31-113, Installation Perimeter Access Control, as supplemented by AFMC and Hill AFB take precedence.
For access to the UTTR Complex, the following criteria must be met:
1) Access has been granted by the appropriate authority after identity proofing and vetting.
2) The individual has a range user point of contact.
3) Access is for official Government business only.
4) The individual possesses valid official photo identification of a type approved by AFI 31-113, as supplemented.
5) The individual complies with all security requirements.
6) The individual signs a Secrecy (Non-disclosure) Agreement, acknowledges the Range Security and Safety Briefing.
7) The individual is a United States Citizen.
UTTR Access Gates, Road Access and the Main Gate Operational hours are 0730 -1700, Monday through Thursday.
All visitors who require access to UTTR facilities must submit a Hill AFB Form 0-74, ten
(10) working days prior to the visit (15 working days prior for groups of 15 or more) to the CO for each visit for Range Squadron approval. Hill AFB Form 0-74 will be completed with the following information:
a) Name and rank
b) Driver License Number and State of Issue
c) Security clearance
d) Job title
e) Date and place of birth
f) If nationalized, provide naturalization number, port of entry, and date
g) Organization
h) Dates of visit
i) Purpose of visit
j) Mode of transportation
k) Entry and exit locations
All property that is being removed from the range shall be accompanied by a property removal pass. Property that is not accompanied by the appropriate removal authorization will be confiscated and held, pending an investigation of the incident.
All Contractor property and equipment must be clearly marked. An inventory shall be submitted of property and equipment that the Contractor will bring on to the Range area. The inventory shall include make, model, and serial number of high value equipment (i.e. power tools, scaffolding, aerial lifts, etc.). Hand tools shall be included on the inventory, listed as “tool box with assorted carpentry tools.” The inventory will be used to issue Property Removal Passes.
All vehicles, personnel, and hand-carried items entering or exiting any range control point, or while on the range, are subject to search and inspection and seizure of any prohibited item at any time. Random, unannounced, and regular searches and inspections will be conducted. These searches and inspections are intended to assure the prohibited articles are not introduced into and government property is not removed, from the range or its facilities.
No POV's will be permitted on UTTR. The Contractor shall transport his personnel from outside the main gate to the work site via their commercial vehicles. The Contractor shall only drive on the approved haul route identified in the Vicinity Map as may be included in individual projects.
Commercial vehicles may be permitted on Range, provided the driver has been authorized by the appropriate authority to drive on range and that the vehicle is currently registered, licensed, insured, and used by personnel who have been authorized range access.
Rental Vehicles are permitted provided a current rental agreement is produced and that the rental vehicle is currently registered, licensed, and used by personnel who have been authorized range access to conduct official business.
Travel by personnel in any area that is outside of their regular assigned duty area is prohibited. Should special assignments require personnel to travel off roads, or into areas where they would not normally be expected to work, prior written permission must be obtained from the Security Administrator and the affected range user.
Sightseeing is strictly prohibited. Personnel who violate this requirement are subject to disciplinary action, withdrawal of access authorization, or arrest and prosecution and termination of contract.
Certain equipment is considered sensitive and without written authorization, this equipment is prohibited from use on the Range. Sensitive equipment shall not be brought onto the Range without specific written authorization from the SABER office located in Building 593 South, Hill AFB. Personnel who are found to be in possession of sensitive equipment without the appropriate authorization will be challenged and the item confiscated pending an investigation. Personnel in possession of sensitive equipment without authorization, or suspected of improper use of sensitive equipment, are subject to withdrawal of access authorization, or arrest and prosecution.
The following is a list of equipment that would be considered “sensitive.” Provided list may not be all inclusive. NOTE: Use of sensitive equipment will be subject to current government restrictions.
1) Recording or copying devices of any type.
2) Electronic equipment that is equipped with a data exchange port which could be used to connect Automated Information System (AIS) equipment. (Excludes items such as pocket computers, wrist watches, or data diaries not equipped with a data exchange port).
3) Computers and associated hardware.
4) Cameras and photograph equipment.
5) Binoculars and optical magnifying equipment.
6) Night Vision Devices.
7) Smartphones and/or personal cellular phones are prohibited in sensitive areas. It is prohibited to use smartphones and personal cellular phones to take photos, video, and/or audio recordings.
Sensitive equipment may be authorized for official use on and removal from the range, to obtain sensitive equipment passes, the Contractor will submit a letter that identifies the personnel who will operate the equipment. Requests for sensitive equipment passes shall contain:
1) Name of the responsible person.
2) Driver License Number and State of Issue.
3) Period of use of the sensitive item.
4) General purposes of use.
5) Method of identification.
6) Identification of item(s) by description, specific serial number, and government control number.
7) Copy of any licensing (e.g. FCC).
Certain items are prohibited on the range. Personnel who are found to be in possession of prohibited items will be challenged and the item confiscated pending an investigation. Personnel in possession of prohibited items are subject to disciplinary action, withdrawal of access authorization, or arrest and prosecution. The following non- government owned items are prohibited on the Range, unless an exception is noted:
1) Alcohol.
2) Controlled substances including illegal drugs and associated paraphernalia, except for prescription medicine.
3) Firearms, ammunition, and other dangerous or deadly weapons.
4) Explosives, incendiary, and explosives or deadly weapons.
5) Weapons: Mace, stun guns, clubs.
6) Two-way radios, CB Radios, Cellular phones (Except two-way or CB radios) which are permanently installed in a commercial vehicle, whose frequency has been approved by the installation commander.
7) Recording or copying devices of any type.
8) Electronic equipment that is equipped with a data exchange port which could be used to connect Automated Information System (AIS) equipment. (Excludes items such as pocket computers, wrist watches, or data diaries that are not equipped with a data exchange port).
9) Computers and associated media.
10) Binoculars, optical magnifying equipment.
11) Night vision devices.
12) Recreational vehicles.
13) Pets, wild or domestic.
14) Children under 18 years of age.
15) Other items prohibited by law.
The Contractor will provide physical security for the materials and work.
43.2 [bookmark: 43.2_UTTR_SECURITY][bookmark: _Toc230075293]UTTR SECURITY
The Contractor shall provide security for the Contractor’s materials and work under their control. If the Contractor elects to provide security personnel, they shall not carry weapons on base, including MACE and night sticks.
It is the Contractors responsibility to notify security forces or security personnel that may be in the area.
44 [bookmark: 44_ENVIRONMENTAL_PROTECTION][bookmark: _Toc230075294]ENVIRONMENTAL PROTECTION
The publications listed below form a part of this specification to the extent referenced. The publications are referred to in the text by the basic designation only. Unless otherwise noted, the latest published version and/or revision shall be used.
HEADQUARTERS, AIR FORCE MATERIAL COMMAND (HQ, AFMC)

APPENDIX Guidance

Air Force Instruction (AFI), Air Force Manual (AFMAN), Hill AFB Instruction (HILLAFBI), Hill AFB Visual Aids (HILLAFBVAs), &/or Other Applicable Legal Requirements

	AFI 32-7001
	Environmental Management

	AFMAN 32-1053
	Integrated Pest Management Program

	AFMAN 32-7003, Chapter 2
	Environmental Conservation – Cultural Resources Management chapter

	AFMAN 32-7003, Chapter 3
	Environmental Conservation – Natural Resources Management chapter

	AFMAN 32-7003, Chapter 3
	Environmental Compliance and Pollution Prevention - Hazardous Materials Management chapter

	AFMAN 32-7003, Chapter 4
	Environmental Compliance and Pollution Prevention – Air Quality Compliance and Resource Management chapter

	AFMAN 32-7003, Chapter 5
	Environmental Compliance and Pollution Prevention – Hazardous Waste Management chapter

	AFMAN 32-7003, Chapter 6
	Environmental Compliance and Pollution Prevention – Integrated Solid Waste Management chapter

	AFMAN 32-7003, Chapter 7
	Environmental Compliance and Pollution Prevention – Toxics Management chapter

	AFI 32-1067
	Water and Fuel Systems

	AFI 32-7044
	Storage Tank Compliance

	HILLAFBI 32-7086
	Hill AFB Hazardous Materials Management

	75 CEG/CEIEA Memorandum, 14
FEB 2020
	Hazardous Materials Management Process (HMMP) for Contractors, Suppliers, and Incoming Deployed Units (IDU) / Temporary Duty (TDY) Units

	HILLAFBVA 32-2
	Hill AFB Environmental Policy

	HILLAFBVA 32-3
	Hill AFB Environmental Policy



	HILLAFBI 32-102
	Hill AFB Environmental Policy

	HILLAFBI 32-104
	Air Quality Compliance

	Hill AFB Management Plan
	Hazardous Waste Management Plan (HWMP)

	Hill AFB AMOP-1
	Asbestos Management and Operating Plan

	Hill AFB LBPMOP-1
	Lead-Based Paint Management and Operations Plan



In order to prevent, and to provide for abatement and control of, any environmental pollution arising from the construction activities of the Contractor in the performance of this contract, Contractors shall comply with all applicable Federal, State, and local laws and regulations, and installation regulations concerning environmental pollution control and abatement.
The Contracting Officer (CO) will notify the Contractor in writing of any noncompliance with the foregoing provisions and the action to be taken. The Contractor shall, after receipt of such notice, immediately take corrective action.
Prior to commencement of the work, the Contractor shall meet with the installation environmental office representatives and the CO to develop mutual understandings relative to compliance with this provision and administration of the environmental pollution control program.
The information provided in this section applies to all other specification sections that are applicable to project.
The Contractor shall provide weigh tickets to the CO monthly for disposal of construction debris and/or recycled materials (i.e. metal doors, aluminum frames, wood doors, etc.) per UFGS, specifically for C&D Waste Management in the Whole Building Design Guide: http://www.wbdg.org/ for additional information.
The work covered by this section consists of furnishing all labor, materials, equipment, and performing all work required for the prevention of environmental pollution during and as the result of construction operations under this contract except for those measures set forth in other sections of these specifications. For the purpose of this specification, environmental pollution is defined as the presence of chemical, physical, or biological elements or agents which adversely affect human life; affect other species of importance to man; or degrade the ability of the environment for aesthetic and recreational purposes. The control of environmental pollution requires consideration of air, water, and land, and involves noise, solid waste-management and management of radiant energy, hazardous materials, radioactive materials, as well as other pollutants.
44.1 [bookmark: 44.1_AIR_QUALITY/EMISSIONS][bookmark: _Toc230075295]AIR QUALITY/EMISSIONS
Any equipment or activity that emits or has the potential to emit pollutants or that disturbs solid or liquid materials, which can become airborne, is a source of air pollution that may require a permit. Activities with anticipated air emissions include but are not limited to painting, chemical, cleaning with degreasers or solvents, material hauling, demolition, sand blasting, use of fuel-burning equipment for industrial heating (other than motor vehicles), fuel storage or dispensing, use of volatile organic compounds or ozone-depleting chemicals, and remediation activities.
Hill Air Force Base - Title V Operating Permit, 1100007003. UTTR - Title V Operating Permit, 300036004.
If air emission estimates for criteria or hazardous air pollutants exceed threshold levels, Contractors shall contact 75th CEG to initiate a construction permit application required by the Utah Division of Air Quality (UDAQ). Contractors shall provide information, as required by the 75th CEG, for construction permit application(s) to the CO for review and approval prior to submittal to UDAQ. Contractors shall be responsible for all fees and associated requirements of the UDAQ.
All new or modified combustion sources will include Low Oxides of Nitrogen Burner Technology. New or modified water heaters will meet R307-230 Ultra-low NOx burner requirements.
For each regulated particulate-emitting activity, the Contractor shall prepare a Fugitive Particulate Control Plan.
Contractors shall ensure all company-owned and employee-owned gasoline and diesel vehicles that shall be driven on the installation comply with the emissions inspection requirements of the applicable air quality zone. CAA section 118(d) AF vehicle I/M program participation excludes all contractors.
The Contractor shall restrict emissions of all smoke and fugitive particulates, to levels less than 20 percent opacity at the point of emission, and to levels that do not visibly disperse beyond installation’s property boundaries unless exempt.
The Contractor shall create no noxious odors.
The maintenance and repair work to air conditioning and refrigeration shall require that best service practices must be put into place and performed to minimize loss of refrigerant during maintenance. Any technician servicing the refrigerant section of the equipment must be certified to handle the specific refrigerant within the machine.
The Contractor shall not vent or cause to be vented Class I Chlorofluorocarbon-based (CFC), Class II Hydrochloroflurocarbon-based (HCFC), and Hydrofluorocarbon-based (HFC) refrigerants to the atmosphere during repair or maintenance work on the equipment covered by this contract.
The Contractor shall have available EPA-certified refrigerant recovery or reclaim equipment to perform the work. All recovered refrigerant shall be turned over to the CO for turn-in to the DLA ODS (Defense Logistics Agency Ozone Depleting Substances) Defense Reserve Stockpile.
Replacement compressors and other replacement equipment used in repairing refrigerant containing systems shall be compatible with the refrigerant within the machine.
The Contractor shall be responsible for meeting all requirements, obtain permits, licensing and certification required by state or local ordnance to work on activities involving more than one acre. All obtained permits and licenses shall be provided to the CO.
The Contractor shall not utilize cutback asphalt or any coating included in the definition of

cutback asphalt during the months of March through September unless the cutback asphalt is used solely as a penetrating prime coat, or there are no emissions of volatile organic compounds from the asphalt under condition of normal use, or the or application is for the paving of parking lots smaller than 300 parking stalls.
Contractors shall not apply sand or gravel to installation roads without obtaining prior written approval from the CO or representative.
Contractor shall ensure all Construction permits and Air Pollutant Emissions Notice’s (APEN’s) are transferred to the installation for inclusion into the installation air operating permit prior to project completion.
44.2 [bookmark: 44.2_WATER_QUALITY][bookmark: _Toc230075296]WATER QUALITY
The Contractor shall comply with the installation Utah Pollutant Discharge Elimination System (UPDES) permit.
If potable water lines are damaged during construction the Contractor must notify the installation Bio-Environmental Engineering (BEE) office immediately. The Contractor shall disinfect all water lines which do not remain full of water under pressure.
Disinfecting shall be in accordance with American Water Works Association Standard 601 and shall not be complete until two consecutive days bacterial samples show no contamination. Bacteriological samples shall be analyzed by a laboratory certified by the State of Utah.
The Contractor shall not dump any restricted materials into the Storm Water Collection System (SWCS). All discharges to the SWCS shall meet Federal, State, and Local regulatory requirements and shall not exceed the installation permit requirements.
The Contractor shall not discharge any non-storm water discharges to the SWCS. Prior approval from the installation environmental office is required for any non-storm water liquid discharge.
The Contractor shall be responsible to produce a Storm Water Pollution Prevention Plan (SWPPP) for review by 75 CEG/CEIE prior to applying for a Notice of Intent (NOI) for a UPDES Construction Permit. Rules and forms are located at http://waterquality.utah.gov/. The Contractor shall provide a copy of the NOI and the SWPPP to the CO upon issuance from state.
The Contractor is responsible for conducting and documenting all storm water inspections as outlined in the UPDES Storm Water Construction General Permit (UTRC00000).
44.3 [bookmark: 44.3_NATURAL_RESOURCES][bookmark: _Toc230075297]NATURAL RESOURCES
The Contractor shall comply with any restrictions of the Endangered Species Act, the Migratory Bird Treaty Act, the Bald and Golden Eagle Protection Act, and forestry requirements of DODI 4715.3 and DODI 7310.5. The Contractor will re-vegetate disturbed areas and protect disturbed ground surfaces from erosion and invasion from invasive plant species. Coordination of seed mixes and seeding methods will be obtained from the Hill AFB Natural Resource Manager and will vary depending on the nature and timing of the project. If any trees are to be removed due to project requirements, a Tree Mitigation Plan must be in place prior to tree removal. This will be coordinated through the Hill AFB Natural Resource Manager. Also refer to installation specific specifications

for requirements.
44.4 [bookmark: 44.4_CULTURAL_RESOURCES][bookmark: _Toc230075298]CULTURAL RESOURCES
The Contractor shall comply with the NHPA of 1966 as amended and codified at 54 USC
§ 300101 et seq; including regulations at 36 CFR Parts 60, 61, 63, 65, 68, 78, 79, and 800 which have been promulgated to implement the Act. This act requires federal agencies to consider historic properties when planning their activities and during any undertaking. An historic property is defined as any prehistoric or historic district, site, building, structure, or object included in, or eligible for, inclusion on the National Register of Historic Places (National Register). This includes all artifacts, records, and material related to the historic properties. Proposed work must follow protocols and guidelines established and detailed in Chapter 2 of AFMANS 32-7003 and Section 7.0 of the Hill AFB, Integrated Cultural Resources Management Plan (ICRMP). The Contractor is responsible for coordinating with the Hill AFB Cultural Resource off to ensure all regulation requirements are met and consultation with interested parties is completed prior to any work being undertaken.
If during construction activities, items are observed that may have historic or archaeological value/interest (e.g., Native American human remains or associated objects, potentially historic objects or structure foundations), the Contractor shall cease all activities that may result in impact to or the destruction of these resources. The Contractor shall prevent his employees from trespassing on, removing, or otherwise disturbing such resources. All items shall be carefully preserved. The Contractor and shall immediately report the find to the CO or representative so that the Hill ABF Culture Resource Program Manager may be notified and a determination made as to their significance and what, if any, special disposition of the finds should be made.
Historic districts contain historically significant structures listed in the State and Federal Register of Historic Places. Prior to any and all work taking place within the boundaries of any historic structure or district, actions must be coordinated through the installation Cultural Resource Manager for National Historic Preservation Act Section 106 Consultation with the Utah State Historical Society. Any work on any National Register eligible history structure or, any work that includes ground disturbance must be coordinated through the installation Culture Resource Manager for National Historic Preservation Act Section 106 Consultation with the Utah State Historical Preservation Office (SHPO).
Any work on historic structures or the associated grounds must comply with the Secretary of The Interior's Standards for the Treatment of Historic Properties, AFI 32- 7065, Cultural Resources Management, as well as State and installation guidance, Hill AFB ICRMP.
44.5 [bookmark: 44.5_SOLID_WASTE_MANAGEMENT][bookmark: _Toc230075299]SOLID WASTE MANAGEMENT
The Contractor shall develop a Waste Management Plan for each TO. Solid Waste Management Plan shall be submitted to the CO and PM within 15 days after notification of contract award unless stated otherwise in TO FOPR. Minimum requirements for the waste management plan shall be:
1) Name of individuals on the Contractor's staff responsible for waste prevention and management.
2) Characterization, including estimated types and quantities, of the waste to be

generated.
3) Name of landfill and/or incinerator to be used and the estimated costs for use, assuming that there would be no salvage or recycling on the project.
4) Identification of local and regional reuse programs, including non-profit organizations such as schools, local housing agencies, and organizations that accept used materials such as materials exchange networks and Habitat for Humanity. Include the name, location, and phone number for each reuse facility to be used.
5) List of specific waste materials that will be salvaged for resale, salvaged and reused on the current project, salvaged and stored for reuse on a future project, or recycled. Identify the recycling facilities by name, location, and phone number.
6) All recyclable material removed shall be recorded on the Hill AFB Construction and Demolition Waste Diversion Report and submitted to the CO, the Government PM, and to the Hill AFB SW Program Manager upon completion of the project.
The Contractor is responsible for handling and disposal of all solid waste generated at the job site. The Contractor shall make all arrangements for disposal of any wastes including wastes requiring special handling such as asbestos, rubble, etc. The Contractor is responsible for all required laboratory testing and any documentation submittals required by the landfill owner. Asphalt containing materials shall be recycled or disposed of in an approved permitted landfill.
The Contractor shall dispose of all construction/demolition and related solid wastes, garbage, and refuse at an off-site solid waste disposal facility possessing the appropriate City or County Certificate of Designation unless otherwise specified.
No waste or materials shall be left on the installation after completion of any project under this contract.
All non-hazardous wastes shall be properly disposed of through a licensed landfill site unless specific provision at the installation allow disposal on the installation property. Demolition rubble shall not be buried anywhere on base or at the work site without permission from the CO. Any cleanups and the costs of these cleanups of improper waste disposals or removals of improperly placed hazardous or landfill restricted waste materials shall be the responsibility of the Contractor.
The Contractor shall participate in the base recycling program or develop a Contractor recycling program. In any event, coordination must be accomplished with theinstallation environmental office. The Contractor shall strive towards a 40% diversion of solid waste from landfills.
The Contractor shall report quarterly and/or at the end of the project, the amount of Non-Hazardous solid waste disposed and non-hazardous solid diverted from land fill by re-use, recycling, donation,and composting.
All carpet and carpet padding should be recycled or diverted from the landfill if possible. The Contractor shall provide certificate of recycling to the CO for all carpet and carpet padding removed.

44.6 [bookmark: 44.6_TOXICS_HAZARDS][bookmark: _Toc230075300]TOXICS HAZARDS
To include but not be limited to asbestos, lead, including lead-based paint, polychlorinated biphenyls (PCBs), and pesticides.
44.6.1 [bookmark: 44.6.1_ASBESTOS][bookmark: _Toc230075301]ASBESTOS
The Contractor shall follow and meet all requirements of the Hill Air Force Asbestos Management and Operating Plan.
The introduction of asbestos-containing materials on the installation is strictly prohibited unless permitted by CO. As required by the installation Bio-environmental Engineering office, building renovation or demolition projects shall require an asbestos survey in order to determine the presence and quantity of material that will be encountered during the project. Any part of the existing building the project may impact shall be included in the survey. The Contractor shall be responsible for ensuring all areas of the project are included in the government provide asbestos reports. If areas of the project are not found in the report, the Contractor shall notify the CO of the discrepancy. Typical suspect materials include floor and/or ceiling tile, tile mastic, roofing materials and flashing mastics, pipe and boiler insulation, wall coverings, sheetrock joint compound, transite materials, etc. The Government will provide the results of any asbestos testing previously accomplished. In addition, the Contractor shall be responsible for all Utah Department of Air Quality asbestos notifications.
The Contractor shall meet all requirements identified by the Utah Division of Air Quality (DAQ) to include Utah DAQ rule R307-801, OSHA 29 CFR 1926.1101 and/or 29 CFR 1910.1001 and EPA 40 CFR Part 61, sub part M.
Hill AFB currently has only two acceptable Asbestos abatement contractors that are approved to work on Hill AFB. They are; Environmental Abatement Inc. (EAI) and Eagle Environmental.
44.6.2 [bookmark: 44.6.2_LEAD-BASED_PAINT_(LBP)][bookmark: _Toc230075302]LEAD-BASED PAINT (LBP)
The Contractor shall follow and meet all the requirements of the Hill Air Force Base Lead-Based Paint Management and Operations Plan.
Existing painted surfaces may contain lead based paint. The Contractor shall keep a steady spray of water on any demolition work that may cause exposures. Runoff shall be contained on the work site to prevent contamination to any watersheds or the sanitary sewer system. The Contractor shall not contaminate the soil with lead due to excessive use of water. The site shall be limited to access by the public and the Contractor is responsible for non-exposure of the public to any lead concentrations above the PEL (Permissible Exposure Level). All removal of lead based paint must be coordinated through the installation environmental office.
The Contractor shall meet all requirements identified by the Utah Division of Air Quality (DAQ) to include Utah DAQ rule R307-840, OSHA 29 CFR 1926.62 and/or 29 CFR 1910.1025 and EPA 40 CFR Part 745.
The Contractor shall ensure building occupants are not exposed to lead above

the OSHA-permissible exposure level by removing them from the work area, isolating the area with physical barriers and warning signs and, if necessary, providing a containment system to ensure other areas are not contaminated by dust and debris. A thorough normal cleanup and washing of the work area must be performed afterwards to ensure all dust and debris isremoved.
Hill AFB currently has only two acceptable LBP abatement contractors that are approved to work on Hill AFB. They are; Environmental Abatement Inc. (EAI) and Eagle Environmental.
44.6.3 [bookmark: 44.6.3_POLYCHLORINATED_BIPHENYLS_(PCB)][bookmark: _Toc230075303]POLYCHLORINATED BIPHENYLS(PCB)
All light ballasts and electrical equipment (transformers, capacitors, etc.) containing PCB materials shall be turned in to the installation Environmental Office.
Units labeled NON PCB do not require special handling or disposal. No equipment containing PCB’s shall be installed during this contract.
Transformers installed during this contract shall be accompanied by a non PCB certification statement and reported to the Civil Engineering Squadron for accountability inventory.
44.6.4 [bookmark: 44.6.4_PESTICIDES][bookmark: _Toc230075304]PESTICIDES
Pesticide is defined as any substance or mixture of substances intended for preventing, destroying, repelling, or migrating any pest, or intended for use as a plant regulator, defoliant or desiccant. Pesticides are considered hazardous materials and must be treated as such, IAW the process outlined in the section below. The term “pests” means arthropods, birds, rodents, nematodes, fungi, bacteria, viruses, algae, snails, marine borers, snakes, weeds, and other organisms (except for human or animal disease-causing organisms) that adversely affect readiness, military operations, or the well-being of personnel and animals; attack or damage real property, supplies, equipment, or vegetation, or are otherwise undesirable.
In order to minimize impacts to existing fauna and flora, the Contractor shall coordinate with the Installation Pest Management Coordinator (IPMC) IAW AFMAN 32-1053 requirement and at least 25 days prior to pesticide application. The Contractor shall discuss integrated pest management strategies with the coordinator and receive concurrence prior to the application of any pesticide associated with these specifications.
Pesticides shall be delivered to the site in the original, unopened containers bearing legible labels indicating the EPA registration number and the manufacturer’s registered uses. Pesticides shall be stored according to manufacturer’s instructions and under lock and key when unattended. Labeling and storage requirements for hazardous materials also apply (see below section). No pesticides are permitted to be mixed on Hill AFB.
The Contractor shall formulate, treat with, and dispose of pesticides and associated containers in accordance with label directions and shall use the

clothing and personal protective equipment specified on the labeling for use during all phases of the application. SDSs shall be available for all pesticide products and provided to the IPMC, as well as IAW the requirements outlined in the Hazardous Materials section below.
Pesticides shall be applied by a State Certified Pesticide Applicator. Water used for formulating shall only come from locations designated by the CO. The Contractor must provide certifications and data on daily pesticide use to the Integrated Pesticides Management Plan (IPMP) or designee, for input into the Enterprise Environmental Safety and Occupational Health – Management Information System (EESOH-MIS).
44.6.5 [bookmark: 44.6.5_HAZARDOUS_MATERIALS/WASTE][bookmark: _Toc230075305]HAZARDOUS MATERIALS/WASTE
All Hazardous Materials (HAZMAT) used, removed, handled, or stored and wastes generated by the Contractor shall be managed in accordance with federal, Air Force, Hill AFB, state and local laws and regulations.
Pre-construction hazardous material reporting requirements: All hazardous materials, regardless of procurement methods or who is using them, must be authorized for use at Hill AFB or other Hill AFB-managed properties.
HAZMAT must also be tracked in EESOH-MIS. All hazardous materials to be brought on-site by the Contractor for use shall be subject to this authorization process and the HAZMAT Management Process (HMMP). This authorization process is performed by and at the discretion of the HMMP Authorizing Offices utilizing EESOH-MIS. The installation reserves the right to prohibit the use of HAZMAT based on these reviews and as related to legal requirements, including air quality permits, and those that the installation deems to be especially hazardous to human health or the environment. The installation also reserves the right to prohibit the use of HAZMAT due to the type and/or quantity of hazardous wastes potentially generated from the HAZMAT. In the event a hazardous material is not authorized for use on installation, the installation may provide the Contractor a list of suitable substitutes; however, the Contractor shall retain responsibility for finding an acceptable substitute. All installations promote waste minimization and pollution prevention practices and the Contractor shall take appropriate actions to comply with these policies.
The following information should be provided to the HMMP Program (75 CEG/CEIEA) 45 days prior to planned activities / commencement of work on site: 1) Identification of CO; 2) Dates of planned work; 3) Type of aircraft or equipment that may be affected; 4) HAZMAT supply sources; 5) Materials Stock Numbers (MSNs), if known; 6) Product trade name as it appears on the containers or Safety Data Sheets (SDSs); 7) Manufacturer, as it appears on containers or SDSs; 8) Container size for each HAZMAT (e.g., 12 ounce can, 5 gallon bucket); 9) Quantity of each HAZMAT planned for use (i.e., count of containers); 10) The most recent SDS for each HAZMAT (if unable to locate a current SDS, please indicate this to the HAZMAT Program POCs; 11) Any relevant Technical Orders (TOs), if known and as applicable; 12) If any of the HAZMAT is an aerosol; 13) If any of the HAZMAT is a kit, and if so, include

the number of components in each kit and the container size for each component; and 14) Length of time the HAZMAT will be used and stored on Hill AFB-managed properties.
Contractors performing work on Hill AFB-managed properties for more than two weeks shall label all HAZMAT with HAZMAT tracking labels (i.e., EESOH-MIS barcode labels) and the manufacturer’s label. For Contractors performing work for two weeks or less, it is up to the discretion of the HMMP Program if HAZMAT tracking labels (i.e., EESOH-MIS barcode labels) are affixed to containers versus immediately available to demonstration authorization status. Labels can be printed by and acquired from the HMMP Program POCs. All HAZMAT must be labeled with the manufacturer’s label that is Globally Harmonized System (GHS) compliant. The Contractor shall also maintain a Hazardous Communications (HAZCOM) program.
Contractors shall document HAZMAT usage, including the MSN, SDS Number, product/trade name, quantity used, unit of measure (e.g., gal, lbs), the date, and an identifier (e.g., contractor company name). These usage reports shall be submitted to the CO and HMMP Program POCs at least quarterly or upon completion of the work if work is completed in less than 90 days.
Contractors that do not follow the above process for authorization and tracking are liable for any associated notices of violations or permit deviations that may result, as well as any associated corrective actions.
The Contractor shall not store HAZMAT on the installation except at the discretion of the installation Environmental Branch. Contractors may be required to ensure all HAZMAT is removed from the installation at the end of the work day and stored off installation.
All hazardous materials used by the Contractor on base shall be stored properly in special areas in accordance with all applicable regulatory requirements. The Contractor shall identify the HAZMAT, the volume, delivering company, the location of storage and estimated storage time if HAZMAT is stored on the installation.
General HAZMAT requirements include but are not limited to keeping containers closed when not in use, posting hazardous warnings and signage as required, checking routinely for leaks and spills, keeping materials at central location, good housekeeping, spill response preventative measures, and use of original containers.
Once the contract is completed, the Contractor shall not leave any HAZMAT including unused liquids, adhesives, or paints on the installation. The Contractor shall notify the HMMP Program POCs and CO of their disposition plan for HAZMAT, once the project is complete, to ensure compliance and conformance with legal requirements.
No HAZMAT is to be sprayed or spilled on the ground, asphalt, or concrete covered surfaces at job sites as a means of disposal. The Contractor shall be charged for any cleanups and disposal costs. All spill cleanups shall be handled

by trained personnel only. The Contractor shall dispose of any hazardous product cleanup in accordance with all applicable regulations.
44.6.6 [bookmark: 44.6.6_HAZARDOUS_WASTE][bookmark: _Toc230075306]HAZARDOUS WASTE
The Contractor shall coordinate all hazardous waste (HAZWASTE) disposals with the installation environmental office. If there is any question about whether or not a substance is classified as hazardous, the Contractor shall contact the installation environmental office. It shall be the responsibility of the Contractor to pay for the disposal of hazardous waste unless otherwise specified.
The Contractor shall handle, accumulate, and manage hazardous waste in accordance with all regulatory requirements and the Hill AFB Hazardous Waste Management Plan.
Fluorescent lamps and batteries for fluorescent light fixtures shall be managed as universal hazardous wastes. PCB containing ballasts from fluorescent light fixtures shall be managed as PCB containing wastes as discussed above.
Fluorescent lamps shall not be disposed of in solid waste dumpsters.
Empty aerosol cans must be managed as universal hazardous waste in accordance with the Hill AFB Hazardous Waste Management Plan. Partially full cans must be disposed of as hazardous universal waste.
Mercury containing equipment including thermostats, will be managed and disposed of as Universal Hazardous Waste.
Batteries will be handled as Universal Hazardous Waste, i.e. Alkaline, Lithium, Nickel-Cadmium and Lithium Ion.
44.6.7 [bookmark: 44.6.7_UNDERGROUND_AND_ABOVE_GROUND_STOR][bookmark: _Toc230075307]UNDERGROUND AND ABOVE GROUND STORAGE TANKS
The Contractor shall meet all requirements of Air Force regulations (AFI 23-201 and AFI 32-7044) and by Federal Government under 40 CFR 112 for above ground storage tanks (ASTs). The Storage Tank Program Manager and Tank Cross-Functional Team should be alerted in advance of any new AST (or other vessel/container used to store fuel or other petroleum, oil or lubricant) installation; certain tanks will require completion of a New Source Sheet. In accordance with 40 CFR Part 280, Utah Code Sections 19-6-401 et seq., and Utah Administrative Code Title R311, underground storage tanks (USTs) greater than 110 gallons require, among other things, permitting, fees, registration, tank and line tightness testing, cathodic protection and testing, secondary containment, under- dispenser containment, reporting and inspections. No new USTs will be allowed without thorough review and approval by 75 CEG/CEIE.
44.6.8 [bookmark: 44.6.8_SPILL_RESPONSE][bookmark: _Toc230075308]SPILL RESPONSE
No hazardous materials are to be sprayed or spilled on the ground, asphalt, or concrete covered surfaces at job sites. The Contractor shall be responsible for any cleanups and disposal costs. Trained personnel shall handle all spill cleanups only. HAZMAT spills greater than 5 gallons or all spills that enter a

water way (storm drain, sanitary drain, or Industrial Waste Water drain) shall be reported immediately to the Hill AFB Fire Dept. by calling 911. HAZMAT spills less than 5 gallons shall be reported to the installation environmental spill phone, (801)-430-3860. A spill report shall be provided to the environmental office detailing the cause of spill, the type and quantity of material spilled and the clean-up actions taken within 3 days of the initial spill. A spill plan may be required for a regulated substance.
Hazardous Material or Hazardous Waste Spill Response procedure:
1) Notify the installation Fire Department immediately of any spills of fuel or other hazardous material or hazardous waste greater than 5 gallons. Smaller spills, less than 5 gallons, should be handled by the Contractor, but shall be coordinated with the installation environmental office. Maintain spill response equipment onsite.
2) Stop source of spill without undue risk of personal injury. Use on-site containment, safety equipment, and materials.
3) Make spill scene off limits to all non-cleanup personnel.
4) Restrict all sources of ignition if flammable material in spill.
5) Report to the installation environmental Office, within 30 minutes.
44.6.9 [bookmark: 44.6.9_SUSTAINABLE_PROCUREMENT_AND_ENVIR][bookmark: _Toc230075309]SUSTAINABLE PROCUREMENT AND ENVIRONMENTAL MANAGEMENT SYSTEM
The Contractor shall perform all work in a manner to minimize pollution, degradation, and exploitation of the environment. The Contractor shall also demonstrate leadership in preventing, controlling and abating environmental pollution by supporting pollution abatement programs and by accelerating corrective measures to meet established standards and criteria.
Procurement of sustainable goods is the purchase of materials made from recycled content or bio-based products that meet EPA guidelines. The Contractor shall support the installation in sustainable procurements and ensure their Sustainable Procurement Process is consistent with DoDI 4105.72, Procurement of Sustainable Goods and Services, AFI 32-7001, and other AF policy and strategies.
Contractor employees shall receive EMS awareness and other appropriate environmental training, and ensure proof of completion available to the CO and EMS Coordinator (75 CEG/CEIEA). EMS training specific to Hill AFB is available from the EMS Coordinator or CO. Contractors shall be aware of their potential and actual impacts to the environment and Mission, and shall be familiar with the message of the Hill AFB Environmental Policy Commitment Statement (HILLAFBI 32-102), which is communicated via HILLAFBVA 32-2 and HILLAFBVA 32-3. The Contractor shall be committed to compliance, reducing risks, pollution prevention, and continual improvement IAW EMS requirements.
44.6.10 [bookmark: 44.6.10_ENVIRONMENTAL_BASELINE_SURVEYS][bookmark: _Toc230075310]ENVIRONMENTAL BASELINE SURVEYS
Environmental Baseline Surveys, also known as Environmental Site

Assessments or Due Diligence Surveys, are studies to indicate existing environmental site conditions. The Contractor shall provide in accordance with AFI 32-7066 if the installation requires documentation for an area such as a Contractor staging area. Upon completion of project and return of Contractor staging area to installation, the Contractor will be held responsible for all clean up actions associated with the staging area.
44.6.11 [bookmark: 44.6.11_NUCLEAR_SOIL_TESTING][bookmark: _Toc230075311]NUCLEAR SOIL TESTING
The Contractor must submit in writing to the CO and Installation Radiation Safety Officer a complete equipment list with nomenclature/serial number(s) and a complete listing of personnel who will be using radioactive source material-containing equipment, along with individual qualifications, specialized training, and certification. Additionally the Contractor shall provide their Agreement-State license and their Nuclear Regulatory Commission (NRC) form 241 at least 72 hours before conducting nuclear soil testing (density). No source material may be taken onto the installation without approval from the Installation Radiation Safety Officer and permission from the appropriate installation commander.
44.6.12 [bookmark: 44.6.12_NOISE][bookmark: _Toc230075312]NOISE
All equipment utilized by the Contractor that produces noise levels in excess of 85 dBA (“A” weighted decibels) must be identified by the Contractor. This equipment will be utilized in a manner that precludes exposure of the occupants or any persons other than Contractor personnel to levels exceeding 85 dBA.
44.6.13 [bookmark: 44.6.13_DEMOLITION][bookmark: _Toc230075313]DEMOLITION
The Contractor shall make all necessary notifications to the CO and 75 CEG.
45 [bookmark: 45_POWDER-ACTUATED_TOOLS][bookmark: _Toc230075314]POWDER-ACTUATED TOOLS
Explosive operated hand tools shall not be used without previous approval of the CO. The Contractor shall comply with OSHA Standard 1926.302(e) when utilizing powder-actuated tools. Storage of explosive cartridges on the installation will be in metal containers and limited to one day’s supply. The Contractor shall provide adequate controls to prevent theft/loss of cartridges used and stored on the installation.
46 [bookmark: 46_CONTRACTOR’S_USE_OF_ELECTROMAGNETIC_E][bookmark: _Toc230075315]CONTRACTOR’S USE OF ELECTROMAGNETIC EMISSION DEVICES
Electromagnetic Emission Devices include: radio/RADAR transmitters, navigational aids, instrumentation’s, signaling, intrusion detection and identification devices, mobile and fixed business radio communication equipment, and Military Auxiliary Radio System (MARS), Citizen Band (CB) radio and amateur radio stations. The Contractor shall comply with the applicable Air Force regulations.
47 [bookmark: 47_FILL_MATERIAL][bookmark: _Toc230075316]FILL MATERIAL
All non-hazardous soils and/or fill materials, including rock, gravel, broken concrete or asphalt, etc. shall be disposed of at an approved off-base landfill.
If an area of construction is in a known area of contamination, the following statement will be in the TO SOW;
There are no remedial actions in place at these locations. Any excavation in an area of industrial activity presents the potential to encounter contaminated soil. Please contact Environmental Restoration or the SABER PM if unusual odors or soil discoloration is observed during any excavation or trenching necessary to complete this project and/or if any monitoring points are encountered.
Additional fill material shall be imported and delivered to the site from off base as a necessary part of project. Material composition shall be subject to the requirements of UFGS Section 31 23
00.00 20, Excavation and Fill. Additional fill may be available from the Hill AFB landfill. If use is not specified in the Government SOW, the Contractor shall request use through a project specific RFI.
48 [bookmark: 48_PAVING_AND_ROADWORK][bookmark: _Toc230075317]PAVING AND ROADWORK
The Contractor shall comply with the recommendations contained in Part 6 of the US Department of Transportation, Federal Highway Administration Manual on Uniform Traffic Control Devices to ensure proper warnings to motorists and adequate traffic control. Traffic control signage should be installed IAW Utah Department of Transportation M&S Standards. All signs, warning lights, barricades, and other traffic control devices shall be provided by the Contractor. The Contractor shall maintain the normal traffic egress to and from the installation during construction at all times. If traffic flow on any roadway is to be modified for any reason, the Contractor must notify the SABER PM and coordinate a road closure by submitting an AF Form 103, Base Civil Engineer Work Clearance Request and traffic coordination plan for approval to the SABER PM thirty (30) Calendar Days prior to commencing with construction activities. The schedule and phasing of roadway lane closure will be discussed in a pre-construction meeting.
49 [bookmark: 49_BASE_REGULATIONS][bookmark: _Toc230075318]BASE REGULATIONS
Contractor employees and visitors are subject to the same restrictions as are Government personnel.
49.1 [bookmark: 49.1_SMOKING/VAPING][bookmark: _Toc230075319]SMOKING/VAPING
The Contractor shall limit the use of tobacco, smoking and vaping to authorized areas only. Tobacco and vaping use shall be IAW applicable installation and DOD policy. No smoking will be allowed within 25 feet of any base facility.
Vaping devices or the use of vaping devices are not allowed in any of the Munition Storage Area (MSA).
49.2 [bookmark: 49.2_SEATBELTS][bookmark: _Toc230075320]SEATBELTS
The use of seatbelts by all vehicle operators and passengers is mandatory on Hill AFB and in the state of Utah. On Hill AFB, vehicle operators and passengers caught not wearing their seatbelts will be issued a traffic citation and may lose their on-base driving privileges.
49.3 [bookmark: 49.3_FIREARMS/ILLEGAL_DRUGS][bookmark: _Toc230075321]FIREARMS/ILLEGAL DRUGS
Firearms or illegal drugs are not allowed on Hill AFB. By accepting a vehicle pass, each person gives their consent to a search of their vehicle while entering, leaving or while on Hill AFB property.
49.4 [bookmark: 49.4_SPEED_LIMIT][bookmark: _Toc230075322]SPEED LIMIT
The speed limits on Hill AFB range from 40 MPH in specified areas, down to 15 MPH, parking lots are 5 MPH.
All contractors and subcontractors are required to follow all traffic regulations while on Hill AFB.
49.5 [bookmark: 49.5_PARKING][bookmark: _Toc230075323]PARKING
Contractor vehicles and equipment will be parked in common parking areas or as otherwise approved in writing by the Facility Manager, SABER PM, and/or CO.
Parking of contractor vehicles shall be restricted to the project parking lot at the location designated by the CO. Under no circumstance shall the Contractor park vehicles and or equipment, even temporarily, on the grass unless approved in advance by the CO. The company name shall be prominently and noticeably displayed on all construction vehicles and equipment parked in the designated spaces. Parking shall not violate fire or safety regulations.
The Contractor shall not park contractor owned equipment or store/stage construction material in common parking lots. All construction material and equipment shall be kept at the Contractors place of business or at the project site until ready for use/install.
49.6 [bookmark: 49.6_CELL_PHONE_USE][bookmark: _Toc230075324]CELL PHONE USE
Use of cell phones while driving is prohibited while on Hill AFB, unless equipped with hands free device. Vehicle operators determined to be talking on a cell phone while driving will be issued a traffic citation and may lose their on-base driving privileges.
50 [bookmark: 50_INAPPROPRIATE_WORKER_BEHAVIOR][bookmark: _Toc230075325]INAPPROPRIATE WORKER BEHAVIOR
The Prime Contractor assumes all responsibility for the actions of all their employees, subcontractors and suppliers while working on Hill AFB.
51 [bookmark: 51_COMPLETION_OF_CONTRACT][bookmark: _Toc230075326]COMPLETION OF CONTRACT
At the conclusion of this contract, the Contractor shall be required to vacate any areas provided to them, including office area(s) and individual work site(s). The Contractor shall return all government provided office area(s) to its original condition and shall do so within 14 calendar days of being notified by the CO, or the conclusion of this contract, whichever comes first.
52 [bookmark: 52_PARTNERING][bookmark: _Toc230075327]PARTNERING
In order to most effectively and efficiently accomplish the work provided under this contract, the Government is encouraging the formation of a cohesive, mutually beneficial partnership with the Contractor and their subcontractors.
This partnership would strive to draw on the strengths, skills and knowledge of each organization in an effort to achieve a quality project, done right the first time, within budget, safely, and on schedule. The focus of partnering is to build cooperative relationships, avoid or minimize disputes and actively pursue the attainment of common goals by the contracting parties. Success will be dependent on teamwork characterized by open communication while always adhering to the highest professional standards. The Contractor shall arrange a partnering meeting between the Government and the Contractor upon request by the CO.
[bookmark: APPENDIX_A:__ABBREVIATIONS/ACRONYMS][bookmark: _Toc230075328]

APPENDIX A: ABBREVIATIONS/ACRONYMS
	AF
	Air Force

	AFB
	Air Force Base

	AFI
	Air Force Instruction

	AIS
	Automated Information System

	BCE
	Base Civil Engineer

	BEE
	Bio-Environmental Engineering

	BFDS
	Base Facility Design Standard

	CAD
	Computer Aided Design

	CCI
	City Cost Index

	CE
	Civil Engineer

	CEG
	Civil Engineer Group

	CES
	Civil Engineer Squadron

	CM
	Contract Manager

	CO
	Contracting Officer

	COR
	Contracting Officers’ Representative

	CPG
	Comprehensive Procurement Guide

	DAQ
	Division of Air Quality

	DoD
	Department of Defense

	DoDI
	Department of Defense Instruction

	DoDM
	Department of Defense Manual

	DV
	Distinguished Visitor

	EPA
	Environmental Protection Agency

	FOPR
	Fair Opportunity Proposal Request

	GFE
	Government Furnished Equipment

	GFM
	Government Furnished Material

	GFP
	Government Furnished Property

	HAZMAT
	Hazardous Materials

	HAZCOM
	Hazardous Communications

	HMMP
	HAZMAT Management Process

	HVAC
	Heating, Ventilation and Air Conditioning



	IAW
	In Accordance With

	IBC
	International Building Code

	IPMC
	Installation Pest Management Coordinator

	MSA
	Munition Storage Area

	MSDS
	Material Safety Data Sheet

	NFPA
	National Fire Protection Agency

	NPI
	Non Pre-Priced Item

	NRC
	Nuclear Regulatory Commission

	O&P
	Overhead & Profit

	OSHA
	Occupational Safety and Health Administration

	PM
	Program Manager or Project Manager

	QASP
	Quality Assurance Surveillance Plan

	QC
	Quality Control

	QCO
	Quality Control Officer

	ROI
	Return on Investment

	SABER
	Simplified Acquisition of Base Engineering Requirements

	SOW
	Statement of Work

	SSHO
	Site Safety and Health Officer

	SWCS
	Storm Water Collection System

	SWPPP
	Storm Water Pollution Prevention Plan

	TO
	Task Order

	UDAQ
	Utah Division of Air Quality

	UFC
	Unified Facilities Criteria

	UFGS
	Unified Facilities Guide Specifications

	UPB
	Unit Price Book

	UPDES
	Utah Pollutant Discharge Elimination System
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	75 ABW Safety Office
	777-7233

	OO-ALC Safety Office
	586-6038

	Command Post
	777-3007

	Security Forces
	777-3056

	Fire Services
	777-3021
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[bookmark: _Toc230075330]SAFETY PRE-BRIEF
Project Title: 	

Location: 	

Brief description of work: 	


Project Number: 	

Contract/Task Order Number: 			

Estimated Start Date: 	

Estimated Completion Date: 	

Safety plan was reviewed by 	Date 	



Contractor: 		Number: 	

Contracting Officer (CO): 	Number: 	

Contracting Officer
Representative (COR): 		Number: 	

Sub-Contractor: 		Number: 	

Site Supervisor: 		Number: 	

75 ABW Safety: 		Number: 777-7233 (SAFE)

OO-ALC Safety: 		Number: 801-586-6038

[bookmark: _Toc230075331]This completed page will be provided to the safety offices for historical purposes
** Construction and manufacturing only

Safety Office Use Only Control number if used (YYYYMMDD-XX)

[bookmark: _Toc230075332]GENERAL SAFETY REQUIREMENTS

This handout is to familiarize you with some of the safety requirements that you may encounter while working on Hill AFB.

The Safety Office sincerely hopes your work here will be mishap free. If you require emergency medical attention, be aware there are no emergency services available at Hill AFB. Emergency service are only available by calling 911.

If you encounter problems with vehicle registration, traffic, parking, or area security you should contact the Security Forces Law Enforcement Desk at 777-3056.

Air Force Materiel Command (AFMC) Acquisition Reform initiatives focus on risk management rather than traditional methods of providing specific government guidance for risk elimination.
With “performance-based” language, the government will provide the Contractor with areas requiring specific information and the Contractor will be free to meet those objectives using corporate standards.

Contractors and their subcontractors are responsible to follow all applicable federal, state, and local laws, Occupational Safety and Health Act, (OSHA) Public Law 91-596, and Air Force guidance called out in this document. Written safety plans will be available to all employees. All work areas will be maintained in a manner that protects all employees, and safeguards the general public, and government personnel, equipment and property.

All employees will be properly trained and qualified and be able to demonstrate knowledge of their duties. All contractors and subcontractors will be knowledgeable of all hazards and potential hazards associated with the duties and the work area they are assigned to. All employees will have the right to stop all work if at any time they deem the duties or area may be hazardous. All hazards will be mitigated prior to work being resumed.

Contractors and subcontractors are responsible for providing any necessary barricades, signs, lights, fencing, and any additional protective measures the Contracting Officer determines is necessary for the purposes of protecting all employees, the general public, government personnel, equipment and property.

Crosswalks: All personnel are required to use the closest crosswalk, or traffic controlled intersection when crossing the road if possible.

**Cranes: If cranes are used, prior to raising the boom above facility roof lines, you must contact 75 Operations Support Squadron (OSS) Airfield Management at 777-3592.

**Dig permits (red stakes): Any digging will require a dig permit from CEG at 777-0540. It may take up to 21 days to get approval, plan accordingly.

Explosive Safety (AFI 91-201) If duties require entry into an explosive clear zone, employees must receive Explosive Safety Awareness Training. Contact your respective Safety Office to schedule a class and receive additional guidance.

Hazardous energy control (LOTO): If lock out tag out procedures are required, a meeting with the area supervisor(s) must take place to coordinate differences in procedures.

**Hot work permits: Any hot work (welding, cutting, grinding…) will require a hot work permit (AF Form 592). Contact the Fire Department at 777-0236.

Motor vehicles: Seatbelts are required while vehicles are in operation. Cell phone use by a driver is prohibited while the vehicle is in motion.

**Permit required confined space entries: If entry into a confined space is required contact the area supervisor and or the installation safety office. All known hazards will be discussed prior to entry. 777-SAFE (7233)

Photography: If photographs will be required, permission to use a camera must be obtained from the unit security manager. Photographs in a secured area will normally not be allowed.

**Trenching/excavations: See dig permits and environmental issues

X-ray approvals: If X-ray equipment will be used contact Bioenvironmental at 777-1053.

Environmental Issues
Air quality: If emission producing equipment is brought on base you must contact Civil Engineering Air Quality Flight at 777-0888. If your process will produce vapors, fumes, or dust you must contact Bioenvironmental at 777-1053.

Cultural resources: If artifacts of any kind are discovered you must contact Civil Engineering Cultural Resources Flight at 586-2464.
Hazardous materials: If any hazardous materials are brought on to the base you must coordinate with Civil Engineering Hazardous Materials Flight at 586-2718.
Hazardous waste: Contact Civil Engineering Hazardous Waste Flight at 586-8537.
Landfill use: If the base landfill will be used you will need to apply for a permit. Contact Civil Engineering Hazardous Solid Waste Flight at 777-5788.

Storm water: Contact Civil Engineering Water Quality Flight at 777-0493.

Flight line
Flight line operations: If you are required to drive on the flight line contact 75 OSS Airfield Management at 777-3592.

[bookmark: _Toc230075333]SAFETY PLAN SPECIFIC REQUIREMENTS
NOTE

[bookmark: _Toc230075334]The government shall assume no liability or responsibility for the Contractor's compliance or non-compliance with safety requirements.

A Safety Plan shall be submitted at the Post Award Conference.

The Contractor must also protect personnel from hazards generated by the work. If the Contractor employs bilingual speaking employees, they must post bilingual signs and have written procedures for specific tasks in applicable languages.

[bookmark: _Toc230075335]Total Case Incident Rate and Days Away, Restricted and Transferred Rates
The offerors shall submit its Total Case Incident Rate (TCIR) and Days Away, Restricted and Transferred (DART) rates, or, injury and illness rates for the past three years. For newly formed entities or other offerors that do not possess three years of consecutive recording data, submit this information for the time period it or they possess. The offeror may also submit other comparable data from a recognized agency, such as workers compensation, insurance rates, etc., for the same time period as well.

Total Case Incident Rate (TCIR) and Days Away, Restricted and Transferred (DART) rates, or, injury and illness rates should be equal to or lower than the most recently published Bureau of Labor Statistics (BLS) national average for North American Industry Classification System (NAICS) 236220. For offerors that do not possess three years of consecutive recording data, submit this information for the time period you do possess. Other comparable data from a recognized agency, such as workers compensation, insurance rates, etc., for the same time period is also acceptable.

Safety program requirements. Contractors will implement a written safety plan, provide it to subcontractors, and have it available upon request at the job site. The plan will consist of the following items if they apply to your work on Hill AFB or any government owned property:
NOTE

[bookmark: _Toc230075336]If safety programs are modified after the initial review, the Contractor shall submit the proposed modification, in writing, to the Contract Administration Office.

a. Hazard Assessments. Prior to any work, a hazard assessment must be conducted, and documented. The assessment will be certified and briefed to all affected employees.

**b. Contractor Safety Board (construction projects). Contractors and subcontractors will display and maintain a safety and health bulletin board in a commonly accessed area in clear view of the on-site workers. The location should be protected against the elements and unauthorized removal. It shall contain, at minimum, the following safety and health information:

*If this information is not posted on the safety board, a placard must indicate its location.

1. A map with route to the nearest Emergency Care Facility.
2. Emergency phone numbers; (911, Police, Fire, Environmental, others as applicable)
3. A copy of the most up-to-date Safety Plan shall be mounted on or adjacent to the bulletin board, or a notice on the bulletin board shall state the location of the Safety Plan. The location of the Safety Plan shall be accessible to all employees.
4. A copy of the current Hazard Analysis/analyses shall be mounted on or adjacent to the bulletin board, or a notice on the bulletin board should state the location of the Hazard Analysis. The location of the Hazard Analysis shall be accessible to all employees.
5. The Occupational Safety and Health Administration (OSHA) Form 300A, Summary of Work Related Injuries and Illnesses, shall be posted, in accordance with OSHA requirements, from February 1 to April 30. It shall be mounted on or adjacent to the bulletin board, which will be accessible to all employees.
6. A copy of the Safety and Occupational Health deficiency tracking log shall be mounted on or be adjacent to the bulletin board or a notice on the bulletin board shall state the location where it may be accessed by all workers upon request.
7. Safety and Health promotional posters.
8. Date of last lost workday injury.
9. OSHA Safety and Health Poster.
10. A copy of the hazardous material inventory, identification of use, approximate quantities and site map detailing location.
11. Mishap reporting forms and hazard reporting forms.
12. Contract Information (Section 1 of this document).

c. Site-specific training. The Contractor will ensure all employees and subcontractor employees are properly trained and qualified to conduct their work safely. Detailed training plans will be developed and available to all employees. Training plans will include, at a minimum, all required information contained in all applicable federal, state, and local laws, Occupational Safety and Health Act, (OSHA) Public Law 91-596, and Air Force guidance called out in this document. The training plans will be available for review upon request from the Contracting or Safety Office.

d. Mishap Reporting (29 CFR 1904) In the event of injury or damage to government equipment or property:
· Contact your supervisor and safety representative.
· Contact your designated Government Representative.
· After hours contact the Hill AFB Command Post at 777-3007.
· Contact your Safety Office representative (75 ABW/SEG or OO-ALC/SEG).
· Secure the mishap scene, do not move anything until released by the Safety Office.
· Obtain witness statements, do not release witnesses until instructed by the Safety Office. Separate witnesses while they are writing statements.

POC: 	  Number: 	 POC: 	  Number: 	 POC: 	  Number: 	

Mishap report shall contain, as a minimum, the following information:
1. Contractor Name, Contract Number, Name and Title of Person(s) Reporting.
2. Date, Time, and exact location of mishap.
3. Narrative of mishap (Events leading to mishap/incident).
4. Cause of mishap, if known.
5. Estimated cost of mishap (material and labor to repair/replace).
6. Nomenclature of equipment and personnel involved in mishap/incident.
7. Corrective actions (taken or proposed).
8. Other pertinent information.

The Contractor will provide copies of Contractor data related to mishaps, such as contractor analyses, test reports, summaries of investigations, etc. as necessary to support the government investigation.

Send a copy of the written mishap/incident report NO LATER THAN 3 work days to the Government Representative, and the Safety Office at 75ABW.SE.Workflow@us.af.mil;

e. Hazardous Communication (HAZCOM, 29 CFR 1910.1200) All materials will have a current Safety Data Sheets available to all employees. Employees will be trained on all aspects of a HAZCOM program.

f. Routine job site inspections. Supervisors are responsible to conduct and document routine safety inspections at intervals established based on potential hazards to the work being conducted. At a minimum a daily area inspection should be conducted.

g. Routine safety briefs. Daily safety briefs will be conducted and documented explaining any new or existing hazardous conditions.

h. On-site competent person. Every worksite will have an assigned competent person to ensure employees and subcontractors are working in a safe manner.

i. Subcontractor Clause. All subcontractors are responsible for following all applicable federal, state, and local laws, Occupational Safety and Health Act, (OSHA) Public Law 91-596, and Air Force guidance called out in this document. Prime Contractors will routinely ensure subcontractors following safety guidance.

j. Identification of segregated work site locations. List any locations or operations that cannot be co-mingled with general industrial operations. Requires Contracting Officer approval of operations and changes at these specific sites.


k. Emergency Action Plans (29 CFR 1926.35, 29 CFR 1910.38) Detailed emergency action plans will be developed and briefed for each site as required. Ensure emergency services are available for extremely hazardous work, examples include but are not limited to permit required confined space entry and fall protection rescue. Ensure this plan is coordinated with Hill AFB Fire Services.

l. Fire Prevention Plans (29 CFR 1926.24, 29 CFR 1910.39) Detailed fire prevention plans will be developed for each work site and briefed to all employees. Ensure this plan is coordinated with Hill AFB Fire Services.


[bookmark: _Toc230075337]**Safety and Occupational Health Plan

The Contractor shall provide a stand-alone Project Health and Safety Plan. The Project Health and Safety Plan shall be kept on-site at the construction management location at all times. All Contractor personnel, subcontractor personnel, Government, and visitors entering the construction site shall be briefed on the health and safety plan and required to sign an endorsement of strict adherence to the plan: USACE EM 385-1-1 Safety and Health Requirements Manual, sets forth the specific Contractor’s Safety Program requirements. The following comprises Health and Safety Plan topics.
a. Background (Site location and history and planned activities).
b. Safety Program Organization (identification of safety program members, roles and responsibilities, contact [normal and emergency] information).
c. Site Map (site delineation, points of entrance and egress, staging areas, alarms and emergency equipment, site evacuation map, and communication devices).
d. Site Hazards (personal safety and environmental).
e. Site Worker Training Requirements.
f. Accident Prevention Plan (APP).
g. Personal Protection Equipment (PPE) Requirements.
h. Activity Hazard Analysis (AHA).
i. Medical Surveillance.
j. Monitoring (frequency, equipment and calibration, action levels).
k. Site Control Areas (requiring PPE, confined spaces).
l. Emergency Response Actions.

The Contractor shall complete a Safety Pre-Brief form, above, for each TO. The form shall be

submitted to the SABER PM within 14 calendar days of TO award for review by the appropriate Safety Office. Once reviewed and signed, the form will be returned to the Contractor. A signed form shall be posted on the Contractors Safety Board. A copy of the Safety Pre-Brief form will be returned to the Contractor. A signed form shall be posted on the Contractors Safety Board.
A copy of the Safety Pre-Brief form will be made available to the Contractors.

